## System_data
| Data | Description
S_base | 100 | Power base of the system [MVA]
Slack_bus | b35 | Slack bus for the simulation
N_freq | 60 | Nominal frequency of the system [Hz]
Max_D_freq | 0.5 | Maximun frequency desviation [Hz/s]
Min_freq | 59.5 | Minimum frequency of the system [Hz]
DB_freq | 0.02 | Dead band governos frequency [Hz]
Delta_1_RF | 0.001388 | Time delta of post-contingency inertia response [h]
Delta_2_RF | 0.004166 | Time delta of primary frequency response [h]
Delta_3_RF | 0.041666 | Time delta of second frequency response [h]

## Bus
| name | vn_kv | type | zone | in_service | min_vm_pu | max_vm_pu | Area_C | SubArea_C | 15_áreas
b1 | Flores_220 | 220 | 1 | Atlantico | TRUE | 0.9 | 1.1 | CARIBE | ATLANTIC | ATL
b2 | Nva_Barranquilla_220 | 220 | 1 | Atlantico | TRUE | 0.9 | 1.1 | CARIBE | ATLANTIC | ATL
b3 | Sabanalarga_220 | 220 | 1 | Atlantico | TRUE | 0.9 | 1.1 | CARIBE | ATLANTIC | ATL
b4 | Sabanalarga_500 | 500 | 1 | Atlantico | TRUE | 0.9 | 1.05 | CARIBE | ATLANTIC | ATL
b5 | Tebsa_220 | 220 | 1 | Atlantico | TRUE | 0.9 | 1.1 | CARIBE | ATLANTIC | ATL
b6 | Caracoli_220 | 220 | 1 | Atlantico | TRUE | 0.9 | 1.1 | CARIBE | ATLANTIC | ATL
b7 | Cuatricent_220 | 220 | 1 | Venezuela_Cuatricentenario | TRUE | 0.9 | 1.1 | CARIBE | CUATRIC | GCM
b8 | Bosque_220 | 220 | 2 | Bolivar | TRUE | 0.9 | 1.1 | CARIBE | BOLIVAR | BOL
b9 | Bolivar_500 | 500 | 1 | Bolivar | TRUE | 0.9 | 1.05 | CARIBE | BOLIVAR | BOL
b10 | Bolivar_220 | 220 | 1 | Bolivar | TRUE | 0.9 | 1.1 | CARIBE | BOLIVAR | BOL
b11 | Cartagena_220 | 220 | 1 | Bolivar | TRUE | 0.9 | 1.1 | CARIBE | BOLIVAR | BOL
b12 | Ternera_220 | 220 | 1 | Bolivar | TRUE | 0.9 | 1.1 | CARIBE | BOLIVAR | BOL
b13 | Candelaria_220 | 220 | 1 | Bolivar | TRUE | 0.9 | 1.1 | CARIBE | BOLIVAR | BOL
b14 | San_Mateo_220 | 220 | 2 | Venezuela_Corozo | TRUE | 0.9 | 1.1 | NORDESTE | COROZO | NDS
b15 | Corozo_220 | 220 | 1 | Venezuela_Corozo | TRUE | 0.9 | 1.1 | NORDESTE | COROZO | NDS
b16 | Cerromatoso_500 | 500 | 1 | Cerromatoso | TRUE | 0.9 | 1.05 | CARIBE | CERROMAT | BOL
b17 | Bacata_220 | 220 | 2 | Bogota | TRUE | 0.9 | 1.1 | ORIENTAL | BOGOTA | BOG
b18 | Bacata_500 | 500 | 2 | Bogota | TRUE | 0.9 | 1.05 | ORIENTAL | BOGOTA | BOG
b19 | Circo_220 | 220 | 1 | Bogota | TRUE | 0.9 | 1.1 | ORIENTAL | BOGOTA | BOG
b20 | Guaca_220 | 220 | 1 | Bogota | TRUE | 0.9 | 1.1 | ORIENTAL | BOGOTA | BOG
b21 | Guavio_220 | 220 | 1 | Bogota | TRUE | 0.9 | 1.1 | ORIENTAL | BOGOTA | BOG
b22 | Mesa_220 | 220 | 2 | Bogota | TRUE | 0.9 | 1.1 | ORIENTAL | BOGOTA | BOG
b23 | Noroeste_220 | 220 | 2 | Bogota | TRUE | 0.9 | 1.1 | ORIENTAL | BOGOTA | BOG
b24 | Paraiso_220 | 220 | 1 | Bogota | TRUE | 0.9 | 1.1 | ORIENTAL | BOGOTA | BOG
b25 | Torca_220 | 220 | 1 | Bogota | TRUE | 0.9 | 1.1 | ORIENTAL | BOGOTA | BOG
b26 | Tunal_220 | 220 | 2 | Bogota | TRUE | 0.9 | 1.1 | ORIENTAL | BOGOTA | BOG
b27 | Chivor_220 | 220 | 1 | Bogota | TRUE | 0.9 | 1.1 | ORIENTAL | BOGOTA | BOG
b28 | Balsillas_220 | 220 | 2 | Bogota | TRUE | 0.9 | 1.1 | ORIENTAL | BOGOTA | BOG
b29 | San_Mateo_EEB_220 | 220 | 2 | Bogota | TRUE | 0.9 | 1.1 | ORIENTAL | BOGOTA | BOG
b30 | Nva_Esperanza_220 | 220 | 1 | Bogota | TRUE | 0.9 | 1.1 | ORIENTAL | BOGOTA | BOG
b31 | Nva_Esperanza_500 | 500 | 1 | Bogota | TRUE | 0.9 | 1.05 | ORIENTAL | BOGOTA | BOG
b32 | Enea_220 | 220 | 1 | CQR | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | CQR | CQR
b33 | San_Felipe_220 | 220 | 1 | CQR | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | CQR | CQR
b34 | Esmeralda_220 | 220 | 1 | CQR | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | CQR | CQR
b35 | La_Miel_220 | 220 | 3 | CQR | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | CQR | CQR
b36 | Virginia_220 | 220 | 2 | CQR | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | CQR | CQR
b37 | Virginia_500 | 500 | 2 | CQR | TRUE | 0.9 | 1.05 | SUROCCIDENTAL | CQR | CQR
b38 | Hermosa_220 | 220 | 1 | CQR | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | CQR | CQR
b39 | Altamira_220 | 220 | 2 | Caqueta | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | CAQUETA | THC
b40 | Jamondino_220 | 220 | 1 | Cauca-Nariño | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | CAUCANAR | CAU
b41 | S_Bernardino_220 | 220 | 1 | Cauca-Nariño | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | CAUCANAR | CAU
b42 | Tesalia_220 | 220 | 1 | Cauca-Nariño | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | CAUCANAR | CAU
b43 | Paez_220 | 220 | 1 | Cauca-Nariño | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | CAUCANAR | CAU
b44 | Betania_220 | 220 | 1 | Huila-Tolima | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | HUILATOL | THC
b45 | Mirolindo(Ibague)_220 | 220 | 1 | Huila-Tolima | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | HUILATOL | THC
b46 | Tuluni_220 | 220 | 1 | Huila-Tolima | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | HUILATOL | THC
b47 | Mocoa_220 | 220 | 2 | Putumayo | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | PUTUMAYO | NPU
b48 | Yumbo_220 | 220 | 1 | Valle | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | VALLE | VAL
b49 | San_Marcos_220 | 220 | 1 | Valle | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | VALLE | VAL
b50 | Juanchito_220 | 220 | 1 | Valle | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | VALLE | VAL
b51 | Alto_Anchya_220 | 220 | 1 | Valle | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | VALLE | VAL
b52 | Pance_220 | 220 | 1 | Valle | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | VALLE | VAL
b53 | San_Marcos_500 | 500 | 1 | Valle | TRUE | 0.9 | 1.05 | SUROCCIDENTAL | VALLE | VAL
b54 | Alferez_220 | 220 | 2 | Valle | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | VALLE | VAL
b55 | Cartago_220 | 220 | 1 | Valle | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | VALLE | VAL
b56 | Salvajina_220 | 220 | 1 | Valle | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | VALLE | VAL
b57 | Copey_220 | 220 | 2 | GCM | TRUE | 0.9 | 1.1 | CARIBE | GCM | GCM
b58 | Fundacion_220 | 220 | 1 | GCM | TRUE | 0.9 | 1.1 | CARIBE | GCM | GCM
b59 | Copey_500 | 500 | 2 | GCM | TRUE | 0.9 | 1.05 | CARIBE | GCM | GCM
b60 | Cuestecita_220 | 220 | 1 | GCM | TRUE | 0.9 | 1.1 | CARIBE | GCM | GCM
b61 | Guajira_220 | 220 | 1 | GCM | TRUE | 0.9 | 1.1 | CARIBE | GCM | GCM
b62 | Santa_Marta_220 | 220 | 2 | GCM | TRUE | 0.9 | 1.1 | CARIBE | GCM | GCM
b63 | Valledupar_220 | 220 | 1 | GCM | TRUE | 0.9 | 1.1 | CARIBE | GCM | GCM
b64 | Termocol_220 | 220 | 1 | GCM | TRUE | 0.9 | 1.1 | CARIBE | GCM | GCM
b65 | R_Cordoba_220 | 220 | 2 | GCM | TRUE | 0.9 | 1.1 | CARIBE | GCM | GCM
b66 | Chinu_500 | 500 | 1 | Cordoba-Sucre | TRUE | 0.9 | 1.05 | CARIBE | CORDOSUC | CSU
b67 | Urra_220 | 220 | 1 | Cordoba-Sucre | TRUE | 0.9 | 1.1 | CARIBE | CORDOSUC | CSU
b68 | Cerromatoso_220 | 220 | 1 | Cordoba-Sucre | TRUE | 0.9 | 1.1 | CARIBE | CORDOSUC | CSU
b69 | Uraba_220 | 220 | 2 | Cordoba-Sucre | TRUE | 0.9 | 1.1 | CARIBE | CORDOSUC | CSU
b70 | Reforma_220 | 220 | 1 | Meta | TRUE | 0.9 | 1.1 | ORIENTAL | META | MGU
b71 | Banadia_220 | 220 | 1 | Arauca | TRUE | 0.9 | 1.1 | NORDESTE | ARAUCA | SAR
b72 | C_Limon_220 | 220 | 2 | Arauca | TRUE | 0.9 | 1.1 | NORDESTE | ARAUCA | SAR
b73 | Samore_220 | 220 | 2 | Arauca | TRUE | 0.9 | 1.1 | NORDESTE | ARAUCA | SAR
b74 | Toledo_220 | 220 | 2 | Arauca | TRUE | 0.9 | 1.1 | NORDESTE | ARAUCA | SAR
b75 | Paipa_220 | 220 | 1 | Boyaca-Casanare | TRUE | 0.9 | 1.1 | NORDESTE | BOYCASAN | BCS
b76 | Sochagota_220 | 220 | 2 | Boyaca-Casanare | TRUE | 0.9 | 1.1 | NORDESTE | BOYCASAN | BCS
b77 | Ocaña_500 | 500 | 2 | Norte de Santander | TRUE | 0.9 | 1.05 | NORDESTE | NSANTAND | NDS
b78 | Cucuta(Belen)_220 | 220 | 2 | Norte de Santander | TRUE | 0.9 | 1.1 | NORDESTE | NSANTAND | NDS
b79 | Ocaña_220 | 220 | 2 | Norte de Santander | TRUE | 0.9 | 1.1 | NORDESTE | NSANTAND | NDS
b80 | Tasajero_220 | 220 | 1 | Norte de Santander | TRUE | 0.9 | 1.1 | NORDESTE | NSANTAND | NDS
b81 | Barranca_220 | 220 | 2 | Santander | TRUE | 0.9 | 1.1 | NORDESTE | SANTANDER | SAR
b82 | Bmanga_220 | 220 | 2 | Santander | TRUE | 0.9 | 1.1 | NORDESTE | SANTANDER | SAR
b83 | Comuneros_220 | 220 | 1 | Santander | TRUE | 0.9 | 1.1 | NORDESTE | SANTANDER | SAR
b84 | Guatiguara_220 | 220 | 1 | Santander | TRUE | 0.9 | 1.1 | NORDESTE | SANTANDER | SAR
b85 | CiraInfanta_220 | 220 | 2 | Santander | TRUE | 0.9 | 1.1 | NORDESTE | SANTANDER | SAR
b86 | Sogamoso_500 | 500 | 2 | Santander | TRUE | 0.9 | 1.05 | NORDESTE | SANTANDER | SAR
b87 | Sogamoso_220 | 220 | 1 | Santander | TRUE | 0.9 | 1.1 | NORDESTE | SANTANDER | SAR
b88 | Palos_220 | 220 | 1 | Santander | TRUE | 0.9 | 1.1 | NORDESTE | SANTANDER | SAR
b89 | Primavera_500 | 500 | 2 | Antioquia | TRUE | 0.9 | 1.05 | ANTIOQUIA | ANTIOQUI | ACH
b90 | Ancon_ISA_220 | 220 | 2 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b91 | Guatape_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b92 | La_Sierra_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b93 | La_Tasajera_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b94 | Occidente_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b95 | Primavera_220 | 220 | 2 | Santander | TRUE | 0.9 | 1.1 | NORDESTE | SANTANDER | SAR
b96 | Purnio_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b97 | San_Carlos_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b98 | San_Carlos_500 | 500 | 1 | Antioquia | TRUE | 0.9 | 1.05 | ANTIOQUIA | ANTIOQUI | ACH
b99 | Jaguas_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b100 | Playas_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b101 | Barbosa_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b102 | Guadalupe_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b103 | Porce_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b104 | Oriente_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b105 | Ancon_EPM_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b106 | Termo_Centro_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b107 | Bello_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b108 | Envigado_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b109 | Miraflores_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b110 | El_Salto_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b111 | Porce_III_500 | 500 | 1 | Antioquia | TRUE | 0.9 | 1.05 | ANTIOQUIA | ANTIOQUI | ACH
b112 | Malena_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.1 | ANTIOQUIA | ANTIOQUI | ACH
b113 | Guayabal_220 | 220 | 1 | Antioquia | TRUE | 0.9 | 1.05 | ANTIOQUIA | ANTIOQUI | ACH
b114 | Pomasqui_220 | 220 | 2 | Ecuador | TRUE | 0.9 | 1.1 | SUROCCIDENTAL | ECUADOR220 | NPU
b115 | Drummond_220 | 220 | 2 | GCM | TRUE | 0.9 | 1.1 | CARIBE | ATLANTIC | GCM
b116 | El_Rio_220 | 220 | 2 | Atlantico | TRUE | 0.9 | 1.1 | CARIBE | ATLANTIC | ATL
b117 | La_Loma_500 | 500 | 2 | GCM | TRUE | 0.9 | 1.05 | CARIBE | GCM | GCM
b118 | Chinu_220 | 220 | 2 | Cordoba-Sucre | TRUE | 0.9 | 1.1 | CARIBE | CORDOSUC | CSU
b119 | Monteria_220 | 220 | 2 | Cordoba-Sucre | TRUE | 0.9 | 1.1 | CARIBE | CORDOSUC | CSU
b120 | San_Antonio_220 | 220 | 2 | Boyaca-Casanare | TRUE | 0.9 | 1.1 | NORDESTE | BOYCASAN | BCS

## Branch
| Name | from | to | R | X | Flowlimit | RATEB | RATEC | Length | V_nom [kV] | N_Lineas | in_service | Area_C | SubArea_C
l1 | El_Rio_220 - Flores_220 | b116 | b1 | 0.0014621 | 0.0076988 | 320 | 320 | 320 | 8 | 220 | 1 | TRUE | CARIBE | ATLANTIC
l2 | El_Rio_220 - Tebsa_220 | b116 | b5 | 0.0013525 | 0.0071214 | 320 | 320 | 320 | 7.4 | 220 | 1 | TRUE | CARIBE | ATLANTIC
l3 | Guatiguara_220 - Sogamoso_220 | b84 | b87 | 0.0029394 | 0.02763 | 388 | 388 | 388 | 54.93 | 220 | 2 | TRUE | NORDESTE | SANTANDER
l4 | Flores_220 - Nva_Barranquilla_220 | b1 | b2 | 0.0013525 | 0.0071214 | 640 | 640 | 640 | 7.4 | 220 | 2 | TRUE | CARIBE | ATLANTIC
l5 | Sabanalarga_220 - Tebsa_220 | b3 | b5 | 0.0022984 | 0.013099 | 800 | 800 | 800 | 38.42 | 220 | 3 | TRUE | CARIBE | ATLANTIC
l6 | Nva_Barranquilla_220 - Sabanalarga_220 | b2 | b3 | 0.0021688 | 0.015213 | 1060 | 1060 | 1060 | 45.28 | 220 | 3 | TRUE | CARIBE | ATLANTIC
l7 | Caracoli_220 - Nva_Barranquilla_220 | b6 | b2 | 0.0022718 | 0.013767 | 320 | 320 | 320 | 13.71 | 220 | 1 | TRUE | CARIBE | ATLANTIC
l8 | Caracoli_220 - Tebsa_220 | b6 | b5 | 0.0016677 | 0.010127 | 320 | 320 | 320 | 10.14 | 220 | 1 | TRUE | CARIBE | ATLANTIC
l9 | Chinu_500 - Sabanalarga_500 | b66 | b4 | 0.00097144 | 0.012051 | 4222 | 4222 | 4222 | 182.52 | 500 | 2 | TRUE | CARIBE | CORDOSUC
l10 | Caracoli_220 - Flores_220 | b6 | b1 | 0.003857 | 0.025041 | 381 | 381 | 381 | 35.9 | 220 | 1 | TRUE | CARIBE | ATLANTIC
l11 | Caracoli_220 - Sabanalarga_220 | b6 | b3 | 0.0036493 | 0.022976 | 381 | 381 | 381 | 30.4 | 220 | 1 | TRUE | CARIBE | ATLANTIC
l12 | Cuatricent_220 - Cuestecita_220 | b7 | b60 | 0.016783 | 0.1434 | 336 | 336 | 336 | 132.0789 | 220 | 1 | TRUE | CARIBE | CUATRIC
l13 | Bosque_220 - Ternera_220 | b8 | b12 | 0.0034236 | 0.024082 | 240 | 240 | 240 | 25.69 | 220 | 1 | TRUE | CARIBE | BOLIVAR
l14 | Bolivar_220 - Bosque_220 | b10 | b8 | 0.0021132 | 0.015572 | 305 | 305 | 305 | 16.85 | 220 | 1 | TRUE | CARIBE | BOLIVAR
l15 | Bolivar_500 - Copey_500 | b9 | b59 | 0.0015796 | 0.022274 | 1650 | 1650 | 1650 | 166.62 | 500 | 1 | TRUE | CARIBE | BOLIVAR
l16 | Sabanalarga_220 - Ternera_220 | b3 | b12 | 0.014794 | 0.082168 | 240 | 240 | 240 | 80.18 | 220 | 1 | TRUE | CARIBE | ATLANTIC
l17 | Bolivar_220 - Cartagena_220 | b10 | b11 | 0.001061 | 0.0069455 | 735 | 735 | 735 | 18.3 | 220 | 2 | TRUE | CARIBE | BOLIVAR
l18 | Bolivar_220 - Sabanalarga_220 | b10 | b3 | 0.0053356 | 0.035894 | 594 | 594 | 594 | 69.91 | 220 | 2 | TRUE | CARIBE | BOLIVAR
l19 | Candelaria_220 - Ternera_220 | b13 | b12 | 0.00028879 | 0.0015971 | 600 | 600 | 600 | 3.12 | 220 | 2 | TRUE | CARIBE | BOLIVAR
l20 | Candelaria_220 - Cartagena_220 | b13 | b11 | 0.00026539 | 0.0014796 | 600 | 600 | 600 | 2.88 | 220 | 2 | TRUE | CARIBE | BOLIVAR
l21 | Corozo_220 - San_Mateo_220 | b15 | b14 | 0.0043998 | 0.01659 | 574 | 574 | 574 | 38.3 | 220 | 2 | TRUE | NORDESTE | COROZO
l22 | Cerromatoso_500 - Primavera_500 | b16 | b89 | 0.0024221 | 0.031644 | 2165 | 2165 | 2165 | 245.15 | 500 | 1 | TRUE | CARIBE | CERROMAT
l23 | Cuestecita_220 - Valledupar_220 | b60 | b63 | 0.019355 | 0.11938 | 228 | 228 | 228 | 116.37 | 220 | 1 | TRUE | CARIBE | GCM
l24 | Cerromatoso_500 - Porce_III_500 | b16 | b111 | 0.0014831 | 0.018681 | 1650 | 1650 | 1650 | 141.52 | 500 | 1 | TRUE | CARIBE | CERROMAT
l25 | Guaca_220 - Mesa_220 | b20 | b22 | 0.00021652 | 0.002336 | 854 | 854 | 854 | 4.71 | 220 | 2 | TRUE | ORIENTAL | BOGOTA
l26 | Circo_220 - Guavio_220 | b19 | b21 | 0.0041447 | 0.044982 | 732 | 732 | 732 | 109.32 | 220 | 2 | TRUE | ORIENTAL | BOGOTA
l27 | Bacata_220 - Torca_220 | b17 | b25 | 0.00098989 | 0.0078883 | 1134 | 1134 | 1134 | 19.88 | 220 | 2 | TRUE | ORIENTAL | BOGOTA
l28 | Bacata_500 - Primavera_500 | b18 | b89 | 0.0018395 | 0.026067 | 1650 | 1650 | 1650 | 196.86 | 500 | 1 | TRUE | ORIENTAL | BOGOTA
l29 | Noroeste_220 - Purnio_220 | b23 | b96 | 0.0055333 | 0.048623 | 740 | 740 | 740 | 102.61 | 220 | 2 | TRUE | ORIENTAL | BOGOTA
l30 | Chivor_220 - Torca_220 | b27 | b25 | 0.0051526 | 0.053141 | 732 | 732 | 732 | 102.84 | 220 | 2 | TRUE | ORIENTAL | BOGOTA
l31 | Chivor_220 - Guavio_220 | b27 | b21 | 0.0012212 | 0.011683 | 778 | 778 | 778 | 22.69 | 220 | 2 | TRUE | ORIENTAL | BOGOTA
l32 | Bacata_220 - Noroeste_220 | b17 | b23 | 0.00026922 | 0.0020821 | 1134 | 1134 | 1134 | 5.46 | 220 | 2 | TRUE | ORIENTAL | BOGOTA
l33 | Balsillas_220 - Mesa_220 | b28 | b22 | 0.0028295 | 0.028523 | 400 | 400 | 400 | 27.61 | 220 | 1 | TRUE | ORIENTAL | BOGOTA
l34 | Balsillas_220 - Noroeste_220 | b28 | b23 | 0.0015049 | 0.014423 | 419 | 419 | 419 | 13.9 | 220 | 1 | TRUE | ORIENTAL | BOGOTA
l35 | Circo_220 - Tunal_220 | b19 | b26 | 0.0027282 | 0.029513 | 366 | 366 | 366 | 29.74 | 220 | 1 | TRUE | ORIENTAL | BOGOTA
l36 | San_Mateo_EEB_220 - Tunal_220 | b29 | b26 | 0.0013724 | 0.014846 | 366 | 366 | 366 | 14.96 | 220 | 1 | TRUE | ORIENTAL | BOGOTA
l37 | Guaca_220 - Paraiso_220 | b20 | b24 | 0.00035122 | 0.0037892 | 732 | 732 | 732 | 7.64 | 220 | 2 | TRUE | ORIENTAL | BOGOTA
l38 | Mesa_220 - Noroeste_220 | b22 | b23 | 0.0042089 | 0.041566 | 381 | 381 | 381 | 40.18 | 220 | 1 | TRUE | ORIENTAL | BOGOTA
l39 | Nva_Esperanza_220 - San_Mateo_EEB_220 | b30 | b29 | 0.0026728 | 0.028911 | 366 | 366 | 366 | 29.407 | 220 | 1 | TRUE | ORIENTAL | BOGOTA
l40 | Chivor_220 - Sochagota_220 | b27 | b76 | 0.0059453 | 0.058111 | 732 | 732 | 732 | 116.03 | 220 | 2 | TRUE | ORIENTAL | BOGOTA
l41 | Guavio_220 - Torca_220 | b21 | b25 | 0.0028162 | 0.040474 | 952 | 952 | 952 | 82.36 | 220 | 2 | TRUE | ORIENTAL | BOGOTA
l42 | Bacata_500 - Nva_Esperanza_500 | b18 | b31 | 0.00053244 | 0.0064444 | 2165 | 2165 | 2165 | 45.9 | 500 | 1 | TRUE | ORIENTAL | BOGOTA
l43 | Guavio_220 - Nva_Esperanza_220 | b21 | b30 | 0.0097851 | 0.14252 | 552 | 552 | 552 | 149.118 | 220 | 1 | TRUE | ORIENTAL | BOGOTA
l44 | Circo_220 - Nva_Esperanza_220 | b19 | b30 | 0.0042008 | 0.045418 | 366 | 366 | 366 | 46.156 | 220 | 1 | TRUE | ORIENTAL | BOGOTA
l45 | Nva_Esperanza_220 - Paraiso_220 | b30 | b24 | 0.00069808 | 0.0075597 | 732 | 732 | 732 | 15.57 | 220 | 2 | TRUE | ORIENTAL | BOGOTA
l46 | Enea_220 - San_Felipe_220 | b32 | b33 | 0.0034641 | 0.032419 | 646 | 646 | 646 | 65.91 | 220 | 2 | TRUE | SUROCCIDENTAL | CQR
l47 | Virginia_220 - Hermosa_220 | b36 | b38 | 0.0030146 | 0.026936 | 381 | 381 | 381 | 27.07 | 220 | 1 | TRUE | SUROCCIDENTAL | CQR
l48 | Esmeralda_220 - Yumbo_220 | b34 | b48 | 0.010974 | 0.092651 | 381 | 381 | 381 | 194.21 | 220 | 2 | TRUE | SUROCCIDENTAL | CQR
l49 | Enea_220 - Esmeralda_220 | b32 | b34 | 0.0017847 | 0.015575 | 646 | 646 | 646 | 31.42 | 220 | 2 | TRUE | SUROCCIDENTAL | CQR
l50 | Mesa_220 - San_Felipe_220 | b22 | b33 | 0.0043784 | 0.039366 | 726 | 726 | 726 | 77.2 | 220 | 2 | TRUE | ORIENTAL | BOGOTA
l51 | Ancon_ISA_220 - Esmeralda_220 | b90 | b34 | 0.013832 | 0.12968 | 381 | 381 | 381 | 129.49 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l52 | Esmeralda_220 - Hermosa_220 | b34 | b38 | 0.0011845 | 0.01067 | 779 | 779 | 779 | 21.84 | 220 | 2 | TRUE | SUROCCIDENTAL | CQR
l53 | Esmeralda_220 - Virginia_220 | b34 | b36 | 0.0013724 | 0.012184 | 750 | 750 | 750 | 23.85 | 220 | 2 | TRUE | SUROCCIDENTAL | CQR
l54 | La_Miel_220 - San_Felipe_220 | b35 | b33 | 0.0033005 | 0.029256 | 760 | 760 | 760 | 58.73 | 220 | 2 | TRUE | SUROCCIDENTAL | CQR
l55 | San_Carlos_500 - Virginia_500 | b98 | b37 | 0.0017569 | 0.026777 | 1732 | 1732 | 1732 | 212.18 | 500 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l56 | La_Miel_220 - Purnio_220 | b35 | b96 | 0.0014444 | 0.012827 | 752 | 752 | 752 | 25.75 | 220 | 2 | TRUE | SUROCCIDENTAL | CQR
l57 | Altamira_220 - Betania_220 | b39 | b44 | 0.00816 | 0.061185 | 396 | 396 | 396 | 82.59 | 220 | 1 | TRUE | SUROCCIDENTAL | CAQUETA
l58 | Altamira_220 - Mocoa_220 | b39 | b47 | 0.014229 | 0.1069 | 396 | 396 | 396 | 144.08 | 220 | 1 | TRUE | SUROCCIDENTAL | CAQUETA
l59 | Altamira_220 - Tesalia_220 | b39 | b42 | 0.0051651 | 0.03837 | 396 | 396 | 396 | 49.7 | 220 | 1 | TRUE | SUROCCIDENTAL | CAQUETA
l60 | Juanchito_220 - Paez_220 | b50 | b43 | 0.0040061 | 0.034732 | 382 | 382 | 382 | 35.19 | 220 | 1 | TRUE | SUROCCIDENTAL | VALLE
l61 | Alferez_220 - S_Bernardino_220 | b54 | b41 | 0.0097895 | 0.097895 | 382 | 382 | 382 | 101.026 | 220 | 1 | TRUE | SUROCCIDENTAL | VALLE
l62 | Paez_220 - S_Bernardino_220 | b43 | b41 | 0.013771 | 0.11607 | 305 | 305 | 305 | 117.97 | 220 | 1 | TRUE | SUROCCIDENTAL | CAUCANAR
l63 | Betania_220 - Tesalia_220 | b44 | b42 | 0.0050097 | 0.026448 | 396 | 396 | 396 | 35.71 | 220 | 1 | TRUE | SUROCCIDENTAL | HUILATOL
l64 | Jamondino_220 - Tesalia_220 | b40 | b42 | 0.027749 | 0.19864 | 266 | 266 | 266 | 263.66 | 220 | 1 | TRUE | SUROCCIDENTAL | CAUCANAR
l65 | Jamondino_220 - Mocoa_220 | b40 | b47 | 0.013603 | 0.080269 | 266 | 266 | 266 | 75.16 | 220 | 1 | TRUE | SUROCCIDENTAL | CAUCANAR
l66 | Betania_220 - S_Bernardino_220 | b44 | b41 | 0.0049077 | 0.06966 | 610 | 610 | 610 | 143.96 | 220 | 2 | TRUE | SUROCCIDENTAL | HUILATOL
l67 | Jamondino_220 - S_Bernardino_220 | b40 | b41 | 0.011601 | 0.093529 | 610 | 610 | 610 | 189.05 | 220 | 2 | TRUE | SUROCCIDENTAL | CAUCANAR
l68 | Mesa_220 - Mirolindo(Ibague)_220 | b22 | b45 | 0.0047968 | 0.043278 | 736 | 736 | 736 | 86.79 | 220 | 2 | TRUE | ORIENTAL | BOGOTA
l69 | Betania_220 - Mirolindo(Ibague)_220 | b44 | b45 | 0.026999 | 0.20551 | 341 | 341 | 341 | 206.11 | 220 | 1 | TRUE | SUROCCIDENTAL | HUILATOL
l70 | Betania_220 - Tuluni_220 | b44 | b46 | 0.021884 | 0.16266 | 341 | 341 | 341 | 158.09 | 220 | 1 | TRUE | SUROCCIDENTAL | HUILATOL
l71 | Mirolindo(Ibague)_220 - Tuluni_220 | b45 | b46 | 0.013977 | 0.10462 | 341 | 341 | 341 | 102.5 | 220 | 1 | TRUE | SUROCCIDENTAL | HUILATOL
l72 | Alferez_220 - Yumbo_220 | b54 | b48 | 0.0023775 | 0.023775 | 382 | 382 | 382 | 24.535 | 220 | 1 | TRUE | SUROCCIDENTAL | VALLE
l73 | Pance_220 - Juanchito_220 | b52 | b50 | 0.003001 | 0.023028 | 421 | 421 | 421 | 22.91 | 220 | 1 | TRUE | SUROCCIDENTAL | VALLE
l74 | San_Marcos_220 - Yumbo_220 | b49 | b48 | 0.00072372 | 0.0062831 | 376 | 376 | 376 | 6.3 | 220 | 1 | TRUE | SUROCCIDENTAL | VALLE
l75 | Juanchito_220 - San_Marcos_220 | b50 | b49 | 0.0024027 | 0.02166 | 375 | 375 | 375 | 21.9 | 220 | 1 | TRUE | SUROCCIDENTAL | VALLE
l76 | Alto_Anchya_220 - Pance_220 | b51 | b52 | 0.0072734 | 0.054066 | 404 | 404 | 404 | 53.91 | 220 | 1 | TRUE | SUROCCIDENTAL | VALLE
l77 | Alto_Anchya_220 - Yumbo_220 | b51 | b48 | 0.0073759 | 0.054636 | 381 | 381 | 381 | 54.67 | 220 | 1 | TRUE | SUROCCIDENTAL | VALLE
l78 | Cartago_220 - San_Marcos_220 | b55 | b49 | 0.0084425 | 0.074959 | 750 | 750 | 750 | 146.72 | 220 | 2 | TRUE | SUROCCIDENTAL | VALLE
l79 | Cartago_220 - Virginia_220 | b55 | b36 | 0.0010108 | 0.0089517 | 750 | 750 | 750 | 17.55 | 220 | 2 | TRUE | SUROCCIDENTAL | VALLE
l80 | Juanchito_220 - Salvajina_220 | b50 | b56 | 0.0083271 | 0.063898 | 421 | 421 | 421 | 63.57 | 220 | 1 | TRUE | SUROCCIDENTAL | VALLE
l81 | Pance_220 - Salvajina_220 | b52 | b56 | 0.0065245 | 0.049997 | 421 | 421 | 421 | 49.73 | 220 | 1 | TRUE | SUROCCIDENTAL | VALLE
l82 | Pance_220 - Yumbo_220 | b52 | b48 | 0.0037156 | 0.027614 | 381 | 381 | 381 | 27.54 | 220 | 1 | TRUE | SUROCCIDENTAL | VALLE
l83 | San_Marcos_500 - Virginia_500 | b53 | b37 | 0.0014315 | 0.021041 | 1732 | 1732 | 1732 | 165.68 | 500 | 1 | TRUE | SUROCCIDENTAL | VALLE
l84 | Copey_220 - Fundacion_220 | b57 | b58 | 0.0091572 | 0.052646 | 456 | 456 | 456 | 49.41 | 220 | 1 | TRUE | CARIBE | GCM
l85 | La_Loma_500 - Ocaña_500 | b117 | b77 | 0.001075 | 0.023919 | 1650 | 1650 | 1650 | 167.97 | 500 | 1 | TRUE | CARIBE | GCM
l86 | Copey_500 - La_Loma_500 | b59 | b117 | 0.00046701 | 0.010391 | 1650 | 1650 | 1650 | 72.97 | 500 | 1 | TRUE | CARIBE | GCM
l87 | Copey_220 - Valledupar_220 | b57 | b63 | 0.0075504 | 0.04748 | 452 | 452 | 452 | 90.8 | 220 | 2 | TRUE | CARIBE | GCM
l88 | Cuestecita_220 - Guajira_220 | b60 | b61 | 0.0088449 | 0.048425 | 480 | 480 | 480 | 95.45 | 220 | 2 | TRUE | CARIBE | GCM
l89 | Fundacion_220 - Sabanalarga_220 | b58 | b3 | 0.0057718 | 0.032351 | 943 | 943 | 943 | 93.5 | 220 | 3 | TRUE | CARIBE | GCM
l90 | Fundacion_220 - R_Cordoba_220 | b58 | b65 | 0.0047826 | 0.031526 | 500 | 500 | 500 | 62.561 | 220 | 2 | TRUE | CARIBE | GCM
l91 | Santa_Marta_220 - Drummond_220 | b62 | b115 | 0.0030455 | 0.020153 | 250 | 250 | 250 | 20 | 220 | 1 | TRUE | CARIBE | GCM
l92 | Santa_Marta_220 - Termocol_220 | b62 | b64 | 0.0021185 | 0.011785 | 250 | 250 | 250 | 11.56 | 220 | 1 | TRUE | CARIBE | GCM
l93 | Guajira_220 - Termocol_220 | b61 | b64 | 0.015082 | 0.083069 | 250 | 250 | 250 | 81.47 | 220 | 1 | TRUE | CARIBE | GCM
l94 | Guajira_220 - Santa_Marta_220 | b61 | b62 | 0.01696 | 0.093306 | 250 | 250 | 250 | 91.51 | 220 | 1 | TRUE | CARIBE | GCM
l95 | R_Cordoba_220 - Santa_Marta_220 | b65 | b62 | 0.0034086 | 0.022556 | 250 | 250 | 250 | 22.385 | 220 | 1 | TRUE | CARIBE | GCM
l96 | R_Cordoba_220 - Drummond_220 | b65 | b115 | 0.00036317 | 0.0024032 | 250 | 250 | 250 | 2.385 | 220 | 1 | TRUE | CARIBE | GCM
l97 | Cerromatoso_220 - Urra_220 | b68 | b67 | 0.0053668 | 0.045233 | 610 | 610 | 610 | 84.61 | 220 | 2 | TRUE | CARIBE | CORDOSUC
l98 | Uraba_220 - Urra_220 | b69 | b67 | 0.0064851 | 0.054658 | 305 | 305 | 305 | 51.12 | 220 | 1 | TRUE | CARIBE | CORDOSUC
l99 | Chinu_500 - Cerromatoso_500 | b66 | b16 | 0.00049016 | 0.0058661 | 6348 | 6348 | 6348 | 136.24 | 500 | 3 | TRUE | CARIBE | CORDOSUC
l100 | Monteria_220 - Chinu_220 | b119 | b118 | 0.0075774 | 0.049659 | 381 | 381 | 381 | 65.49 | 220 | 1 | TRUE | CARIBE | CORDOSUC
l101 | Monteria_220 - Uraba_220 | b119 | b69 | 0.015226 | 0.099788 | 381 | 381 | 381 | 131.6 | 220 | 1 | TRUE | CARIBE | CORDOSUC
l102 | Guavio_220 - Reforma_220 | b21 | b70 | 0.0057998 | 0.067267 | 549 | 549 | 549 | 81.13 | 220 | 1 | TRUE | ORIENTAL | BOGOTA
l103 | Reforma_220 - Tunal_220 | b70 | b26 | 0.0026403 | 0.030352 | 732 | 732 | 732 | 74.95 | 220 | 2 | TRUE | ORIENTAL | META
l104 | Jamondino_220 - Pomasqui_220 | b40 | b114 | 0.005445 | 0.054755 | 1612 | 1612 | 1612 | 215.23 | 220 | 4 | TRUE | SUROCCIDENTAL | CAUCANAR
l105 | Banadia_220 - C_Limon_220 | b71 | b72 | 0.012201 | 0.094767 | 305 | 305 | 305 | 86.46 | 220 | 1 | TRUE | NORDESTE | ARAUCA
l106 | Banadia_220 - Samore_220 | b71 | b73 | 0.0072251 | 0.056108 | 305 | 305 | 305 | 51.2 | 220 | 1 | TRUE | NORDESTE | ARAUCA
l107 | Palos_220 - Toledo_220 | b88 | b74 | 0.00814 | 0.078102 | 305 | 305 | 305 | 73.23 | 220 | 1 | TRUE | NORDESTE | SANTANDER
l108 | Samore_220 - Toledo_220 | b73 | b74 | 0.0062972 | 0.048623 | 331 | 331 | 331 | 44.69 | 220 | 1 | TRUE | NORDESTE | ARAUCA
l109 | Guatiguara_220 - Sochagota_220 | b84 | b76 | 0.0084963 | 0.072395 | 697 | 697 | 697 | 142.2 | 220 | 2 | TRUE | NORDESTE | SANTANDER
l110 | Paipa_220 - Sochagota_220 | b75 | b76 | 0.00022787 | 0.0025419 | 942 | 942 | 942 | 5.19 | 220 | 2 | TRUE | NORDESTE | BOYCASAN
l111 | San_Antonio_220 - Sochagota_220 | b120 | b76 | 0.0016754 | 0.011557 | 762 | 762 | 762 | 30.6 | 220 | 2 | TRUE | NORDESTE | BOYCASAN
l112 | Cucuta(Belen)_220 - San_Mateo_220 | b78 | b14 | 0.0011755 | 0.009131 | 305 | 305 | 305 | 8.53 | 220 | 1 | TRUE | NORDESTE | NSANTAND
l113 | Cucuta(Belen)_220 - Tasajero_220 | b78 | b80 | 0.0017246 | 0.012699 | 310 | 310 | 310 | 11.45 | 220 | 1 | TRUE | NORDESTE | NSANTAND
l114 | Guatiguara_220 - Tasajero_220 | b84 | b80 | 0.014269 | 0.12787 | 376 | 376 | 376 | 127.63 | 220 | 1 | TRUE | NORDESTE | SANTANDER
l115 | Ocaña_220 - San_Mateo_220 | b79 | b14 | 0.016118 | 0.12782 | 333 | 333 | 333 | 120.57 | 220 | 1 | TRUE | NORDESTE | NSANTAND
l116 | Ocaña_220 - Palos_220 | b79 | b88 | 0.021507 | 0.17116 | 338 | 338 | 338 | 160.39 | 220 | 1 | TRUE | NORDESTE | NSANTAND
l117 | Palos_220 - Tasajero_220 | b88 | b80 | 0.014213 | 0.11133 | 312 | 312 | 312 | 101.46 | 220 | 1 | TRUE | NORDESTE | SANTANDER
l118 | San_Mateo_220 - Tasajero_220 | b14 | b80 | 0.0025801 | 0.019161 | 328 | 328 | 328 | 18.75 | 220 | 1 | TRUE | NORDESTE | COROZO
l119 | Barranca_220 - Sogamoso_220 | b81 | b87 | 0.0086488 | 0.053027 | 343 | 343 | 343 | 52.26 | 220 | 1 | TRUE | NORDESTE | SANTANDER
l120 | Bmanga_220 - Sogamoso_220 | b82 | b87 | 0.0073977 | 0.045356 | 343 | 343 | 343 | 44.7 | 220 | 1 | TRUE | NORDESTE | SANTANDER
l121 | Barranca_220 - Comuneros_220 | b81 | b83 | 0.001632 | 0.012046 | 308 | 308 | 308 | 10.91 | 220 | 1 | TRUE | NORDESTE | SANTANDER
l122 | Bmanga_220 - Guatiguara_220 | b82 | b84 | 0.0017865 | 0.012818 | 319 | 319 | 319 | 12.11 | 220 | 1 | TRUE | NORDESTE | SANTANDER
l123 | Bmanga_220 - Palos_220 | b82 | b88 | 0.0038179 | 0.023862 | 343 | 343 | 343 | 23.45 | 220 | 1 | TRUE | NORDESTE | SANTANDER
l124 | CiraInfanta_220 - Comuneros_220 | b85 | b83 | 0.0026828 | 0.01759 | 114 | 114 | 114 | 17.29 | 220 | 1 | TRUE | NORDESTE | SANTANDER
l125 | Comuneros_220 - Guatiguara_220 | b83 | b84 | 0.010331 | 0.09341 | 308 | 308 | 308 | 95.24 | 220 | 1 | TRUE | NORDESTE | SANTANDER
l126 | Comuneros_220 - Primavera_220 | b83 | b95 | 0.0082528 | 0.062694 | 617 | 617 | 617 | 111.6 | 220 | 2 | TRUE | NORDESTE | SANTANDER
l127 | Guatiguara_220 - Palos_220 | b84 | b88 | 0.0038878 | 0.03056 | 319 | 319 | 319 | 30.6 | 220 | 1 | TRUE | NORDESTE | SANTANDER
l128 | Guatiguara_220 - Primavera_220 | b84 | b95 | 0.018279 | 0.16044 | 373 | 373 | 373 | 162.93 | 220 | 1 | TRUE | NORDESTE | SANTANDER
l129 | Ocaña_500 - Sogamoso_500 | b77 | b86 | 0.0017808 | 0.021606 | 1650 | 1650 | 1650 | 163.68 | 500 | 1 | TRUE | NORDESTE | NSANTAND
l130 | Primavera_500 - Sogamoso_500 | b89 | b86 | 0.0015141 | 0.017963 | 1650 | 1650 | 1650 | 135.67 | 500 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l131 | Ancon_EPM_220 - Ancon_ISA_220 | b105 | b90 | 2.2965e-05 | 0.00019157 | 800 | 800 | 800 | 0.38 | 220 | 2 | TRUE | ANTIOQUIA | ANTIOQUI
l132 | Primavera_500 - San_Carlos_500 | b89 | b98 | 0.00084494 | 0.010734 | 2165 | 2165 | 2165 | 82.61 | 500 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l133 | Jaguas_220 - Malena_220 | b99 | b112 | 0.0088837 | 0.075239 | 293 | 293 | 293 | 69.35 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l134 | Playas_220 - Primavera_220 | b100 | b95 | 0.012008 | 0.10292 | 374 | 374 | 374 | 104.34 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l135 | Ancon_EPM_220 - Miraflores_220 | b105 | b109 | 0.0024174 | 0.020302 | 296 | 296 | 296 | 20 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l136 | Barbosa_220 - Guadalupe_220 | b101 | b102 | 0.0062041 | 0.051754 | 296 | 296 | 296 | 51.33 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l137 | Barbosa_220 - Guatape_220 | b101 | b91 | 0.0044238 | 0.036902 | 296 | 296 | 296 | 36.6 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l138 | Barbosa_220 - La_Tasajera_220 | b101 | b93 | 0.001459 | 0.014392 | 307 | 307 | 307 | 14.5 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l139 | Barbosa_220 - Miraflores_220 | b101 | b109 | 0.0064302 | 0.05364 | 296 | 296 | 296 | 53.2 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l140 | Barbosa_220 - Porce_220 | b101 | b103 | 0.0060281 | 0.052703 | 349 | 349 | 349 | 52.1 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l141 | Barbosa_220 - El_Salto_220 | b101 | b110 | 0.0051028 | 0.044325 | 349 | 349 | 349 | 44.5 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l142 | Bello_220 - La_Tasajera_220 | b107 | b93 | 0.0019339 | 0.016241 | 349 | 349 | 349 | 16 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l143 | Bello_220 - El_Salto_220 | b107 | b110 | 0.0082432 | 0.068975 | 349 | 349 | 349 | 68.2 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l144 | Envigado_220 - Guatape_220 | b108 | b91 | 0.0075876 | 0.063139 | 296 | 296 | 296 | 63.1 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l145 | Envigado_220 - Occidente_220 | b108 | b94 | 0.0029109 | 0.028715 | 307 | 307 | 307 | 28.93 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l146 | Envigado_220 - Oriente_220 | b108 | b104 | 0.0031745 | 0.026416 | 296 | 296 | 296 | 26.4 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l147 | Guadalupe_220 - Occidente_220 | b102 | b94 | 0.0089756 | 0.081234 | 296 | 296 | 296 | 81.2 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l148 | Guadalupe_220 - Porce_220 | b102 | b103 | 0.00022971 | 0.0020817 | 349 | 349 | 349 | 2.04 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l149 | Guadalupe_220 - El_Salto_220 | b102 | b110 | 0.0010636 | 0.0089327 | 296 | 296 | 296 | 8.8 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l150 | Guatape_220 - Jaguas_220 | b91 | b99 | 0.00098235 | 0.0086022 | 748 | 748 | 748 | 18.65 | 220 | 2 | TRUE | ANTIOQUIA | ANTIOQUI
l151 | Guatape_220 - Miraflores_220 | b91 | b109 | 0.0062368 | 0.052026 | 296 | 296 | 296 | 51.6 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l152 | Guatape_220 - Oriente_220 | b91 | b104 | 0.0045574 | 0.037923 | 296 | 296 | 296 | 37.9 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l153 | Guatape_220 - Playas_220 | b91 | b100 | 0.0025576 | 0.021335 | 296 | 296 | 296 | 21.16 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l154 | La_Tasajera_220 - Occidente_220 | b93 | b94 | 0.0023203 | 0.022888 | 307 | 307 | 307 | 23.06 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l155 | Malena_220 - Primavera_220 | b112 | b95 | 0.0012056 | 0.0089544 | 293 | 293 | 293 | 8.23 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l156 | Oriente_220 - Playas_220 | b104 | b100 | 0.0066175 | 0.055202 | 296 | 296 | 296 | 54.75 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l157 | Porce_220 - El_Salto_220 | b103 | b110 | 0.0012251 | 0.011073 | 349 | 349 | 349 | 10.9 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l158 | Guatape_220 - San_Carlos_220 | b91 | b97 | 0.001589 | 0.017922 | 880 | 880 | 880 | 35.77 | 220 | 2 | TRUE | ANTIOQUIA | ANTIOQUI
l159 | La_Sierra_220 - Primavera_220 | b92 | b95 | 0.0085718 | 0.067376 | 309 | 309 | 309 | 59.78 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l160 | La_Sierra_220 - San_Carlos_220 | b92 | b97 | 0.0048762 | 0.031995 | 309 | 309 | 309 | 30.18 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l161 | Porce_III_500 - San_Carlos_500 | b111 | b98 | 0.001116 | 0.01403 | 1650 | 1650 | 1650 | 106.44 | 500 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l162 | San_Carlos_220 - Ancon_ISA_220 | b97 | b90 | 0.005927 | 0.055267 | 740 | 740 | 740 | 107.04 | 220 | 2 | TRUE | ANTIOQUIA | ANTIOQUI
l163 | La_Sierra_220 - Purnio_220 | b92 | b96 | 0.0056462 | 0.050059 | 750 | 750 | 750 | 100.47 | 220 | 2 | TRUE | ANTIOQUIA | ANTIOQUI
l164 | Termo_Centro_220 - Primavera_220 | b106 | b95 | 0.00053687 | 0.0040948 | 674 | 674 | 674 | 8.21 | 220 | 2 | TRUE | ANTIOQUIA | ANTIOQUI
l165 | Purnio_220 - San_Carlos_220 | b96 | b97 | 0.0054003 | 0.043514 | 738 | 738 | 738 | 91.39 | 220 | 2 | TRUE | ANTIOQUIA | ANTIOQUI
l166 | Ancon_EPM_220 - Guayabal_220 | b105 | b113 | 0.0026982 | 0.024742 | 381 | 381 | 381 | 24.64 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l167 | Bello_220 - Guayabal_220 | b107 | b113 | 0.0025022 | 0.023558 | 381 | 381 | 381 | 22.85 | 220 | 1 | TRUE | ANTIOQUIA | ANTIOQUI
l168 | Cerromatoso_500 - Cerromatoso_220 | b16 | b68 | 1e-12 | 0.077084 | 360 | 360 | 360 |  |  |  |  | CARIBE | CERROMAT
l169 | Sabanalarga_500 - Sabanalarga_220 | b4 | b3 | 1e-12 | 0.034187 | 1350 | 1350 | 1350 |  |  |  |  | CARIBE | ATLANTIC
l170 | Bolivar_500 - Bolivar_220 | b9 | b10 | 1e-12 | 0.049658 | 900 | 900 | 900 |  |  |  |  | CARIBE | BOLIVAR
l171 | Bacata_500 - Bacata_220 | b18 | b17 | 1e-12 | 0.099752 | 450 | 450 | 450 |  |  |  |  | ORIENTAL | BOGOTA
l172 | Nva_Esperanza_500 - Nva_Esperanza_220 | b31 | b30 | 1e-12 | 0.10106 | 450 | 450 | 450 |  |  |  |  | ORIENTAL | BOGOTA
l173 | Virginia_500 - Virginia_220 | b37 | b36 | 1e-12 | 0.10184 | 450 | 450 | 450 |  |  |  |  | SUROCCIDENTAL | CQR
l174 | San_Marcos_500 - San_Marcos_220 | b53 | b49 | 1e-12 | 0.10193 | 450 | 450 | 450 |  |  |  |  | SUROCCIDENTAL | VALLE
l175 | Copey_500 - Copey_220 | b59 | b57 | 1e-12 | 0.050331 | 900 | 900 | 900 |  |  |  |  | CARIBE | GCM
l176 | Ocaña_500 - Ocaña_220 | b77 | b79 | 1e-12 | 0.037601 | 720 | 720 | 720 |  |  |  |  | NORDESTE | NSANTAND
l177 | Sogamoso_500 - Sogamoso_220 | b86 | b87 | 1e-12 | 0.033193 | 1350 | 1350 | 1350 |  |  |  |  | NORDESTE | SANTANDER
l178 | San_Carlos_500 - San_Carlos_220 | b98 | b97 | 1e-12 | 0.034043 | 1350 | 1350 | 1350 |  |  |  |  | ANTIOQUIA | ANTIOQUI
l179 | Primavera_500 - Primavera_220 | b89 | b95 | 1e-12 | 0.099665 | 450 | 450 | 450 |  |  |  |  | ANTIOQUIA | ANTIOQUI
l180 | Chinu_220 - Chinu_500 | b118 | b66 | 1e-12 | 0.096093 | 450 | 450 | 450 |  |  |  |  | CARIBE | CORDOSUC

## SM_Unit
| Name | Bus_Name | Bus_number | c | b | a | CSU | V_nom | PF | Pmin | Pmax | Qmin | Qmax | Min_ON | Min_OFF | Ramp_UP | Ramp_Down | IniT_ON | Init_off | IniMW | Slack | In_service | Area | SubArea
g1 | Flores 1 Gas | Flores_220 | b1 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 44 | 108 | -45.7884 | 94.0464 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | ATLANTIC
g2 | Flores 1 Vapor | Flores_220 | b1 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 21 | 52 | -17.297 | 35.0757 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | ATLANTIC
g3 | Tebsa Gas 110 1 | Tebsa_220 | b5 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 50 | 92 | -35.7445 | 78.5902 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | ATLANTIC
g4 | Tebsa Gas 220 1 | Tebsa_220 | b5 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 50 | 92.2 | -34.958 | 77.8867 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | ATLANTIC
g5 | Tebsa Vapor 1 | Tebsa_220 | b5 | 0 | 0 | 0 | 0 | 18 | 0.85 | 0 | 165.22 | -35.0742 | 103.7401 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | ATLANTIC
g6 | Flores IV Gen2 | Flores_220 | b1 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 36 | 106 | -60 | 66 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | ATLANTIC
g7 | Flores IV Gen4 | Flores_220 | b1 | 0 | 0 | 0 | 0 | 16.5 | 0.85 | 92 | 172 | -77 | 110 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | ATLANTIC
g8 | Flores IV Gen3 | Flores_220 | b1 | 0 | 0 | 0 | 0 | 18 | 0.85 | 92 | 172 | -90 | 100 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | ATLANTIC
g9 | Brrquilla 3 | Tebsa_220 | b5 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 33 | 64 | -30 | 56 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | ATLANTIC
g10 | Brrquilla 4 | Tebsa_220 | b5 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 33 | 63 | -30 | 55 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | ATLANTIC
g11 | Tebsa Gas 220 2 | Tebsa_220 | b5 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 50 | 92.2 | -34.9919 | 77.8851 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | ATLANTIC
g12 | Tebsa Gas 220 3 | Tebsa_220 | b5 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 50 | 92.2 | -34.9622 | 77.8314 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | ATLANTIC
g13 | Tebsa Vapor 2 | Tebsa_220 | b5 | 0 | 0 | 0 | 0 | 18 | 0.85 | 0 | 165.22 | -35.1247 | 103.7403 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | ATLANTIC
g14 | Tebsa Gas 110 2 | Tebsa_220 | b5 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 50 | 92 | -35.794 | 78.5903 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | ATLANTIC
g15 | Autog Unibol | Caracoli_220 | b6 | 0 | 0 | 0 | 0 | 13.2 | 0.8 | 0 | 1.1 | 0 | 4.9 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | ATLANTIC
g16 | Cuatricentenario | Cuatricent_220 | b7 | 0 | 0 | 0 | 0 | 220 | 0.9 | 0 | 180 | -87.2 | 87.2 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | CUATRIC
g17 | Candelaria 1 | Candelaria_220 | b13 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 65 | 157 | -54.6486 | 107.8378 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | BOLIVAR
g18 | Candelaria 2 | Candelaria_220 | b13 | 0 | 0 | 0 | 0 | 18 | 0.85 | 65 | 157 | -40.7838 | 108.1622 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | BOLIVAR
g19 | Cartagena 1 | Cartagena_220 | b11 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 27 | 61 | 0 | 30 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | BOLIVAR
g20 | Cartagena 3 | Cartagena_220 | b11 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 27 | 66 | 0 | 30 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | BOLIVAR
g21 | Proelectrica 1 | Cartagena_220 | b11 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 42 | 45 | -10.2 | 40.5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | BOLIVAR
g22 | Proelectrica 2 | Cartagena_220 | b11 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 42 | 45 | -13.3 | 41.9 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | BOLIVAR
g23 | Cartagena 2 | Cartagena_220 | b11 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 27 | 61 | 0 | 30 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | BOLIVAR
g24 | Autog Argos Cartagena | Candelaria_220 | b13 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 9.9 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | BOLIVAR
g25 | Autog Reficar Ecop | Candelaria_220 | b13 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 9.9 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | BOLIVAR
g26 | Corozo | Corozo_220 | b15 | 0 | 0 | 0 | 0 | 220 | 0.9 | 0 | 135 | -65.4 | 65.4 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | COROZO
g27 | Gecelca III | Cerromatoso_220 | b68 | 0 | 0 | 0 | 0 | 18 | 0.85 | 90 | 164 | -114.65 | 114.65 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | CORDOSUC
g28 | Gecelca 32 | Cerromatoso_500 | b16 | 0 | 0 | 0 | 0 | 19 | 0.85 | 130 | 273 | -189 | 189 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | CERROMAT
g29 | Menor Providencia | Cerromatoso_500 | b16 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 4.9 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | CERROMAT
g30 | Menor Doña Juana II | Circo_220 | b19 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 9.88 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | BOGOTA
g31 | Paraiso 1 | Paraiso_220 | b24 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 34 | 92 | -33 | 40 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g32 | Guaca 1 | Paraiso_220 | b24 | 0 | 0 | 0 | 0 | 13.8 | 0.93 | 40 | 108 | -42 | 42 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g33 | Charquito | Nva_Esperanza_220 | b30 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 19.4 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g34 | Limonar Granada | Nva_Esperanza_500 | b31 | 0 | 0 | 0 | 0 | 6.9 | 0.84 | 0 | 18 | -0.1 | 11 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g35 | Menor Sueva | Torca_220 | b25 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 6 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g36 | Chivor UG1 | Chivor_220 | b27 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 10 | 125 | -60 | 60 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g37 | Chivor UG5 | Chivor_220 | b27 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 10 | 125 | -59 | 60 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g38 | Guavio 1 | Guavio_220 | b21 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 60 | 250 | -128.4632 | 168.4947 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g39 | Chivor UG2 | Chivor_220 | b27 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 10 | 125 | -55 | 60 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g40 | Chivor UG3 | Chivor_220 | b27 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 10 | 125 | -61 | 60 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g41 | Chivor UG4 | Chivor_220 | b27 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 10 | 125 | -59 | 61 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g42 | Chivor UG6 | Chivor_220 | b27 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 10 | 125 | -53 | 60 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g43 | Chivor UG7 | Chivor_220 | b27 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 10 | 125 | -53 | 60 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g44 | Chivor UG8 | Chivor_220 | b27 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 10 | 125 | -50 | 60 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g45 | Zipa 3 | Chivor_220 | b27 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 31 | 63 | -0.1 | 20 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | BOGOTA
g46 | Zipa 2 | Chivor_220 | b27 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 17 | 34 | 0 | 14 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | BOGOTA
g47 | Menor Santa Ana | Torca_220 | b25 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 8 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | BOGOTA
g48 | Guaca 2 | Paraiso_220 | b24 | 0 | 0 | 0 | 0 | 13.8 | 0.93 | 40 | 108 | -42 | 42 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g49 | Guaca 3 | Paraiso_220 | b24 | 0 | 0 | 0 | 0 | 13.8 | 0.93 | 40 | 108 | -42 | 42 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g50 | Paraiso 2 | Paraiso_220 | b24 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 34 | 92 | -43 | 43 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g51 | Paraiso 3 | Paraiso_220 | b24 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 34 | 92 | -33 | 40 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g52 | PCH Tunjita | Chivor_220 | b27 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 4 | 19.7242 | -14.98 | 14.78 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | BOGOTA
g53 | Zipa 4 | Chivor_220 | b27 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 31 | 64 | -0.1 | 20 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | BOGOTA
g54 | Zipa 5 | Chivor_220 | b27 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 31 | 63 | -0.1 | 20 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | BOGOTA
g55 | Guavio 2 | Guavio_220 | b21 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 60 | 250 | -128.4632 | 168.4947 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g56 | Guavio 3 | Guavio_220 | b21 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 60 | 250 | -128.4632 | 168.4947 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g57 | Guavio 4 | Guavio_220 | b21 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 60 | 250 | -128.4632 | 168.4947 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g58 | Guavio 5 | Guavio_220 | b21 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 60 | 250 | -15 | 15 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g59 | PCH Usaquen | Torca_220 | b25 | 0 | 0 | 0 | 0 | 11.4 | 0.9 | 0.386 | 1.74 | -1.12 | 0.85 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g60 | PCH Suba | Torca_220 | b25 | 0 | 0 | 0 | 0 | 11.4 | 0.9 | 0.448 | 2.55 | -1.682 | 1.311 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g61 | Dario Valencia Samper 1 | Guaca_220 | b20 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 5 | 50 | -29 | 37 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g62 | Dario Valencia Samper 2 | Guaca_220 | b20 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 5 | 50 | -25.3636 | 42.4545 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g63 | Dario Valencia Samper 5 | Guaca_220 | b20 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 5 | 50 | -18 | 37 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g64 | Salto II U2 | Nva_Esperanza_220 | b30 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 5 | 35 | -20 | 20 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ORIENTAL | BOGOTA
g65 | Laguneta G1 | Nva_Esperanza_220 | b30 | 0 | 0 | 0 | 0 | 6.9 | 0.8 | 10 | 18 | -5 | 13 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | BOGOTA
g66 | PCH La Naveta | Guaca_220 | b20 | 0 | 0 | 0 | 0 | 4.16 | 0.9 | 0.4 | 4.8 | -3.276 | 3.78 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | BOGOTA
g67 | Menor Doña Juana | Circo_220 | b19 | 0 | 0 | 0 | 0 | 0.48 | 0.8 | 0.8 | 1.7 | -1.19 | 1.25 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | BOGOTA
g68 | Autog Guavio | Guavio_220 | b21 | 0 | 0 | 0 | 0 | 4.16 | 0.8 | 1 | 9.9 | 0 | 1 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | BOGOTA
g69 | Cog CocaCola 2.44 MW | Chivor_220 | b27 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 2.44 | -3.645 | 5.638 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | BOGOTA
g70 | Tequendama 1 | Nva_Esperanza_500 | b31 | 0 | 0 | 0 | 0 | 13.8 | 0.866 | 0.5 | 14.2 | -7.8 | 10.4 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | BOGOTA
g71 | Tequendama 2 | Nva_Esperanza_500 | b31 | 0 | 0 | 0 | 0 | 13.8 | 0.866 | 0.5 | 14.2 | -7.8 | 10.4 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | BOGOTA
g72 | Tequendama 3 | Nva_Esperanza_220 | b30 | 0 | 0 | 0 | 0 | 13.8 | 0.866 | 0.5 | 14.2 | -7.8 | 10.4 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | BOGOTA
g73 | Tequendama 4 | Nva_Esperanza_500 | b31 | 0 | 0 | 0 | 0 | 13.8 | 0.866 | 0.5 | 14.2 | -7.8 | 10.4 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | BOGOTA
g74 | PCH Montebonito | San_Felipe_220 | b33 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 19.9 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CQR
g75 | La Miel 1 | La_Miel_220 | b35 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 20 | 132 | -80 | 92 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 1 | 1 | SUROCCIDENTAL | CQR
g76 | Esmeralda 1 | Esmeralda_220 | b34 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 0 | 15 | -8 | 9.4 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CQR
g77 | San Fcisco 1 | Esmeralda_220 | b34 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 12 | 45 | -24 | 27 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CQR
g78 | Insula 3 | Esmeralda_220 | b34 | 0 | 0 | 0 | 0 | 4.2 | 0.8 | 0 | 7 | -0.1 | 3 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CQR
g79 | Insula 1 | Esmeralda_220 | b34 | 0 | 0 | 0 | 0 | 4.2 | 0.8 | 0 | 6 | -0.1 | 3 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CQR
g80 | PCH Bosque | Hermosa_220 | b38 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 2.4 | -0.05 | 1.5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CQR
g81 | Dorada | Purnio_220 | b96 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 10 | 51 | -19 | 50 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g82 | Menor Rionegro | Purnio_220 | b96 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 9.6 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g83 | La Miel 2 | La_Miel_220 | b35 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 20 | 132 | -64.1988 | 77.2237 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CQR
g84 | La Miel 3 | La_Miel_220 | b35 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 20 | 132 | -64.1988 | 78.2485 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CQR
g85 | Esmeralda 2 | Esmeralda_220 | b34 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 0 | 15 | -8 | 9.4 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CQR
g86 | Insula 2 | Esmeralda_220 | b34 | 0 | 0 | 0 | 0 | 4.2 | 0.8 | 0 | 6 | -0.1 | 3 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CQR
g87 | San Fcisco 2 | Esmeralda_220 | b34 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 12 | 45 | -24 | 27 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CQR
g88 | San Fcisco 3 | Esmeralda_220 | b34 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 12 | 45 | -31 | 36 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CQR
g89 | Menor Belmonte | Hermosa_220 | b38 | 0 | 0 | 0 | 0 | 13.2 | 0.8 | 1 | 3.4 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CQR
g90 | Menor Nuevo Libaré | Hermosa_220 | b38 | 0 | 0 | 0 | 0 | 13.2 | 0.9 | 1.5 | 5.1 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CQR
g91 | Menor San Jose | San_Felipe_220 | b33 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.38 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CQR
g92 | Ingenio Risaralda 1 | Esmeralda_220 | b34 | 0 | 0 | 0 | 0 | 13.2 | 0.8 | 0.5 | 17 | 0 | 12 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CQR
g93 | Menor Morro Azul | Esmeralda_220 | b34 | 0 | 0 | 0 | 0 | 13.2 | 0.9 | 3.41 | 19.9 | -2 | 2 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CQR
g94 | PCH El Eden | San_Felipe_220 | b33 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 19.9 | -6.244 | 10.706 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CQR
g95 | Menor La Frisolera | Esmeralda_220 | b34 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0.1 | 0.468 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CQR
g96 | Menor Intermedia | Enea_220 | b32 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.96 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CQR
g97 | Menor San Cancio | Enea_220 | b32 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 2 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CQR
g98 | Menor Municipal | Enea_220 | b32 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 1.4 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CQR
g99 | Menor Guacaica | Enea_220 | b32 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.86 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CQR
g100 | Menor Bayona | Hermosa_220 | b38 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.6 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CQR
g101 | Menor Campestre | Hermosa_220 | b38 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.7 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CQR
g102 | Menor Union | Hermosa_220 | b38 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.7 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CQR
g103 | Menor Guachicono | S_Bernardino_220 | b41 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 12.08 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CAUCANAR
g104 | Menor EgiptoyPalmas | Paez_220 | b43 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 4.4 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CAUCANAR
g105 | Cog Incauca 60MW | Paez_220 | b43 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 0 | 60 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CAUCANAR
g106 | PCH Patico II | S_Bernardino_220 | b41 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 15.9 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CAUCANAR
g107 | Florida 1 | S_Bernardino_220 | b41 | 0 | 0 | 0 | 0 | 13.8 | 0.87 | 0 | 9.95 | -0.1 | 9 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CAUCANAR
g108 | Rio Mayo 1 | Jamondino_220 | b40 | 0 | 0 | 0 | 0 | 6.6 | 0.9 | 6 | 6.6 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CAUCANAR
g109 | Quimbo 1 | Tesalia_220 | b42 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 50 | 198 | -135.9737 | 127.1053 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CAUCANAR
g110 | Quimbo 2 | Tesalia_220 | b42 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 50 | 198 | -135.9737 | 127.1053 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CAUCANAR
g111 | Florida 2 | S_Bernardino_220 | b41 | 0 | 0 | 0 | 0 | 13.8 | 0.87 | 0 | 9.95 | -0.1 | 9 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CAUCANAR
g112 | Rio Mayo 2 | Jamondino_220 | b40 | 0 | 0 | 0 | 0 | 6.6 | 0.9 | 6 | 6.6 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CAUCANAR
g113 | Rio Mayo 3 | Jamondino_220 | b40 | 0 | 0 | 0 | 0 | 6.6 | 0.9 | 6 | 6.6 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CAUCANAR
g114 | PCH San Francisco | Jamondino_220 | b40 | 0 | 0 | 0 | 0 | 13.2 | 0.9 | 0.1 | 0.468 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CAUCANAR
g115 | Cogen Proenca | Paez_220 | b43 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 19.9 | -21.75 | 31.875 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | CAUCANAR
g116 | Menor Rio Bobo | Jamondino_220 | b40 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 4 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CAUCANAR
g117 | Menor Julio Bravo | Jamondino_220 | b40 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 1.5 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CAUCANAR
g118 | Menor Rio Sapuyes | Jamondino_220 | b40 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 1.65 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CAUCANAR
g119 | Menor Rio Palo | Paez_220 | b43 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 1.44 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CAUCANAR
g120 | Menor Sajandi | S_Bernardino_220 | b41 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 3.2 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CAUCANAR
g121 | Menor Mondomo | Paez_220 | b43 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.75 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CAUCANAR
g122 | Menor Silvia | S_Bernardino_220 | b41 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.38 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CAUCANAR
g123 | Menor Patico Cabrera | S_Bernardino_220 | b41 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 1.48 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CAUCANAR
g124 | Menor Coconuco | S_Bernardino_220 | b41 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 4.5 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CAUCANAR
g125 | Cogen Proenca II | Paez_220 | b43 | 0 | 0 | 0 | 0 | 13.2 | 0.85 | 7 | 17 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CAUCANAR
g126 | Ambeima 1 | Tuluni_220 | b46 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 22.5 | -9.1071 | 9.1071 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | HUILATOL
g127 | Ambeima 2 | Tuluni_220 | b46 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 22.5 | -9.1071 | 9.1071 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | HUILATOL
g128 | PCH Buco | Betania_220 | b44 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 1.36 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | HUILATOL
g129 | Betania 1 | Betania_220 | b44 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 60 | 168.75 | -96.5556 | 85.4444 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | HUILATOL
g130 | Prado 4 | Tuluni_220 | b46 | 0 | 0 | 0 | 0 | 4.2 | 0.92 | 0 | 5 | -0.1 | 3 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | HUILATOL
g131 | Prado 1 | Tuluni_220 | b46 | 0 | 0 | 0 | 0 | 6.6 | 0.92 | 1 | 17 | -8 | 9 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | HUILATOL
g132 | Amoya 1 | Tuluni_220 | b46 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 4 | 40 | -23.3114 | 27.3114 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | HUILATOL
g133 | Amoya 2 | Tuluni_220 | b46 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 4 | 40 | -23.3114 | 27.3114 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | HUILATOL
g134 | Cucuana 1 | Mirolindo(Ibague)_220 | b45 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 3 | 28 | -10.34 | 8.72 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | HUILATOL
g135 | Cucuana 2 | Mirolindo(Ibague)_220 | b45 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 3 | 28 | -10.34 | 8.72 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | HUILATOL
g136 | PCH Currucucues | Mirolindo(Ibague)_220 | b45 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 1.25 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | HUILATOL
g137 | Betania 2 | Betania_220 | b44 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 60 | 168.75 | -96.5556 | 85.4444 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | HUILATOL
g138 | Betania 3 | Betania_220 | b44 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 60 | 168.75 | -96.5556 | 85.4444 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | HUILATOL
g139 | Prado 2 | Tuluni_220 | b46 | 0 | 0 | 0 | 0 | 6.6 | 0.92 | 1 | 17 | -8 | 9 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | HUILATOL
g140 | Prado 3 | Tuluni_220 | b46 | 0 | 0 | 0 | 0 | 6.6 | 0.92 | 1 | 17 | -8 | 9 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | HUILATOL
g141 | Menor T Piedras | Mirolindo(Ibague)_220 | b45 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 3.75 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | HUILATOL
g142 | PCH Coello | Mirolindo(Ibague)_220 | b45 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0.2 | 1.2 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | HUILATOL
g143 | Menor La Pita | Betania_220 | b44 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 1.42 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | HUILATOL
g144 | Menor Iquira I | Betania_220 | b44 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 4.32 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | HUILATOL
g145 | Menor Iquira II | Betania_220 | b44 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 5.4 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | HUILATOL
g146 | Menor Inza | Betania_220 | b44 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.75 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | HUILATOL
g147 | Menor Mirolindo | Mirolindo(Ibague)_220 | b45 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 3.75 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | HUILATOL
g148 | Menor Ventana A | Mirolindo(Ibague)_220 | b45 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 2.5 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | HUILATOL
g149 | Menor Ventana B | Mirolindo(Ibague)_220 | b45 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 2.5 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | HUILATOL
g150 | Menor Rio Recio | Mirolindo(Ibague)_220 | b45 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.3 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | HUILATOL
g151 | Menor Pastales | Mirolindo(Ibague)_220 | b45 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.7 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | HUILATOL
g152 | El Cairo - Argos 6.5 MW | Yumbo_220 | b48 | 0 | 0 | 0 | 0 | 115 | 0.8 | 0 | 5.2 | -6.5 | 6.5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | VALLE
g153 | PCH Dovio | Cartago_220 | b55 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 14.2 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g154 | PCH Rio Bravo | San_Marcos_220 | b49 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 15.86 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g155 | PCH Flautas | San_Marcos_220 | b49 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 5.8 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g156 | PCH Rio Grande | San_Marcos_220 | b49 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 8.7 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g157 | PCH Río Frazadas | San_Marcos_500 | b53 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 9.9 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g158 | Alto Anchya 1 | Alto_Anchya_220 | b51 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 30 | 120 | -44 | 48 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | VALLE
g159 | Bajo Anchya 1 | Yumbo_220 | b48 | 0 | 0 | 0 | 0 | 6.9 | 0.9 | 1 | 13 | -7.6667 | 8.6667 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | VALLE
g160 | Bajo Anchya 3 | Yumbo_220 | b48 | 0 | 0 | 0 | 0 | 6.9 | 0.98 | 5 | 24 | -10.6154 | 11.6154 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | VALLE
g161 | Calima 1 | San_Marcos_500 | b53 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 16 | 33 | -29 | 20 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g162 | Emcali Gas | Yumbo_220 | b48 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 65 | 149 | -55 | 114 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g163 | Emcali Vapor | Yumbo_220 | b48 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 35 | 80 | -30 | 76 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g164 | Salvajina 1 | Salvajina_220 | b56 | 0 | 0 | 0 | 0 | 13.8 | 0.9542 | 60 | 125 | -26 | 29 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | VALLE
g165 | TValle Gas | Yumbo_220 | b48 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 68 | 140 | -88 | 123 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g166 | TValle Vapor | Yumbo_220 | b48 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 32 | 62 | -32 | 66 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g167 | PCH Alto Tulua 1 | San_Marcos_220 | b49 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 2.5 | 9.95 | 0 | 5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | VALLE
g168 | CHP Incauca | Juanchito_220 | b50 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 0 | 10 | -14.1 | 24.3 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | VALLE
g169 | CHP Ingenio San Carlos | San_Marcos_220 | b49 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 2 | -2.04 | 5.25 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | VALLE
g170 | CHP Providencia | Yumbo_220 | b48 | 0 | 0 | 0 | 0 | 13.2 | 0.8 | 0 | 19.9 | -15 | 30 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | VALLE
g171 | PCH Amaime 1 | Yumbo_220 | b48 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 4.675 | 9.585 | 0 | 4.35 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | VALLE
g172 | Salvajina 2 | Salvajina_220 | b56 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 30 | 95 | -46 | 63 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g173 | Salvajina 3 | Salvajina_220 | b56 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 60 | 95 | -46 | 46 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | VALLE
g174 | Alto Anchya 2 | Alto_Anchya_220 | b51 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 30 | 120 | -33.0494 | 38.0793 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | VALLE
g175 | Alto Anchya 3 | Alto_Anchya_220 | b51 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 30 | 120 | -64 | 72 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | VALLE
g176 | Bajo Anchya 4 | Yumbo_220 | b48 | 0 | 0 | 0 | 0 | 6.9 | 0.98 | 5 | 24 | -10.6154 | 11.6154 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | VALLE
g177 | Bajo Anchya 2 | Yumbo_220 | b48 | 0 | 0 | 0 | 0 | 6.9 | 0.9 | 1 | 13 | -7.3333 | 8.3333 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | VALLE
g178 | Calima 2 | San_Marcos_500 | b53 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 16 | 33 | -24.2611 | 17.1567 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | VALLE
g179 | Calima 3 | San_Marcos_500 | b53 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 16 | 33 | -29 | 20 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g180 | Calima 4 | San_Marcos_500 | b53 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 16 | 33 | -29 | 20 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g181 | PCH Amaime 2 | Yumbo_220 | b48 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 4.675 | 9.585 | 0 | 4.35 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | SUROCCIDENTAL | VALLE
g182 | PCH Bajo Tulua 1 | San_Marcos_220 | b49 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 1 | 10 | -5.18 | 4.83 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g183 | PCH Bajo Tulua 2 | San_Marcos_500 | b53 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 5 | 10 | -5.18 | 4.83 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g184 | Cog Mayaguez 1 | Juanchito_220 | b50 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 19.9 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g185 | Gen Ingenio Rio Paila | Cartago_220 | b55 | 0 | 0 | 0 | 0 | 13.2 | 0.8 | 0 | 16 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g186 | Menor Nima | Yumbo_220 | b48 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 6.7 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g187 | Menor RFrio I | San_Marcos_220 | b49 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 1.67 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g188 | Menor RFrio II 1 | San_Marcos_500 | b53 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0.5 | 5 | -2.7 | 4.7 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g189 | Menor Rio Cali 1 | Pance_220 | b52 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 1 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g190 | Menor Rio Cali 2 | Pance_220 | b52 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.8 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g191 | Menor Rumor | San_Marcos_220 | b49 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 2.5 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g192 | PCH El Cocuyo | Cartago_220 | b55 | 0 | 0 | 0 | 0 | 0.48 | 0.9 | 0 | 0.7 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g193 | PCH Alto Tulua 2 | San_Marcos_220 | b49 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 2.5 | 9.95 | 0 | 5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g194 | Menor RFrio II 2 | San_Marcos_220 | b49 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0.5 | 5 | -2.7 | 4.7 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g195 | CHP Castilla | Juanchito_220 | b50 | 0 | 0 | 0 | 0 | 4.16 | 0.85 | 0 | 3 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g196 | Menor Ovejas | Pance_220 | b52 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.82 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g197 | Menor Asnazu | Pance_220 | b52 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.45 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g198 | Autog Argos Yumbo | Yumbo_220 | b48 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 10 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g199 | Ingenio Manuelita | Yumbo_220 | b48 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 3.5 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g200 | Cogenerador Manuelita 2 12 MW | Yumbo_220 | b48 | 0 | 0 | 0 | 0 | 13.2 | 0.8 | 0 | 12 | -18.75 | 18.75 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
g201 | La Luna U1 | La_Loma_500 | b117 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 330 | -115 | 127.5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
g202 | La Luna U2 | La_Loma_500 | b117 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 330 | -115 | 127.5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
g203 | Guajira 1 | Guajira_220 | b61 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 72 | 143 | -40 | 40 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | GCM
g204 | Jepirachi | Cuestecita_220 | b60 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 18.42 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | GCM
g205 | Guajira 2 | Guajira_220 | b61 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 72 | 143 | -40 | 40 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | GCM
g206 | Termonorte U1 | Termocol_220 | b64 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 2.7 | 8.8 | -3 | 4 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
g207 | MTequendama Fund | Fundacion_220 | b58 | 0 | 0 | 0 | 0 | 13.8 | 0.81 | 0.35 | 2.25 | -1.67 | 1 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
g208 | Termonorte U6 | Termocol_220 | b64 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 2.7 | 8.8 | -3 | 4 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
g209 | Termonorte U2 | Termocol_220 | b64 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 2.7 | 8.8 | -3 | 4 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
g210 | Termonorte U3 | Termocol_220 | b64 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 2.7 | 8.8 | -3 | 4 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
g211 | Termonorte U4 | Termocol_220 | b64 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 2.7 | 8.8 | -3 | 4 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
g212 | Termonorte U5 | Termocol_220 | b64 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 2.7 | 8.8 | -3 | 4 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
g213 | Termonorte U7 | Termocol_220 | b64 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 2.7 | 8.8 | -3 | 4 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
g214 | Termonorte U8 | Termocol_220 | b64 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 2.7 | 8.8 | -3 | 4 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
g215 | Termonorte U9 | Termocol_220 | b64 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 2.7 | 8.8 | -3 | 4 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
g216 | Termonorte U10 | Termocol_220 | b64 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 2.7 | 8.8 | -3 | 4 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
g217 | Termosolar Awarala 19.9 MW | Bolivar_220 | b10 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 19.9 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | BOLIVAR
g218 | Urra 1 | Urra_220 | b67 | 0 | 0 | 0 | 0 | 13.8 | 0.92 | 50 | 83 | -36 | 47.5714 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | CORDOSUC
g219 | Urra 2 | Urra_220 | b67 | 0 | 0 | 0 | 0 | 13.8 | 0.92 | 50 | 85 | -35.6667 | 47.5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | CORDOSUC
g220 | Urra 3 | Urra_220 | b67 | 0 | 0 | 0 | 0 | 13.8 | 0.92 | 50 | 85 | -35.6667 | 47.5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | CORDOSUC
g221 | Urra 4 | Urra_220 | b67 | 0 | 0 | 0 | 0 | 13.8 | 0.92 | 50 | 85 | -35.6667 | 47.5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | CARIBE | CORDOSUC
g222 | Autog Argos Toluviejo | Bolivar_220 | b10 | 0 | 0 | 0 | 0 | 6.9 | 0.8 | 0 | 3.7 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | BOLIVAR
g223 | Ocoa | Reforma_220 | b70 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 47.04 | 0 | 20 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | META
g224 | Menor Bioenergy | Reforma_220 | b70 | 0 | 0 | 0 | 0 | 13.2 | 0.8 | 0 | 19.9 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | META
g225 | Autog Yaguarito | Reforma_220 | b70 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 1.6 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | META
g226 | TermoCapachos | Banadia_220 | b71 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 4.8 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | ARAUCA
g227 | Paipa 1 | Paipa_220 | b75 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 18 | 36 | -7.6667 | 33.5556 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | NORDESTE | BOYCASAN
g228 | Paipa 2 | Paipa_220 | b75 | 0 | 0 | 0 | 0 | 13.8 | 0.93 | 35 | 72 | -32 | 49 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | BOYCASAN
g229 | Paipa 3 | Paipa_220 | b75 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 35 | 70 | -16.5882 | 34.3529 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | NORDESTE | BOYCASAN
g230 | Yopal 2 | San_Antonio_220 | b120 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 22 | 30 | -7 | 20 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | NORDESTE | BOYCASAN
g231 | M_El Morro_1 | San_Antonio_220 | b120 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 15 | 19.9 | -4 | 11 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | NORDESTE | BOYCASAN
g232 | M_El Morro_2 | San_Antonio_220 | b120 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 15 | 19 | -4 | 11 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | NORDESTE | BOYCASAN
g233 | M_Cimarron | San_Antonio_220 | b120 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 15 | 20 | -4 | 11 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | NORDESTE | BOYCASAN
g234 | MYopal 1 | San_Antonio_220 | b120 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 15 | 19.9 | -4 | 11 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | NORDESTE | BOYCASAN
g235 | Paipa 4 | Paipa_220 | b75 | 0 | 0 | 0 | 0 | 16 | 0.8 | 50 | 154 | -42.3846 | 132.7692 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | NORDESTE | BOYCASAN
g236 | Yopal 3 | San_Antonio_220 | b120 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 0 | 40 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | BOYCASAN
g237 | Yopal 4 | San_Antonio_220 | b120 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 0 | 40 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | BOYCASAN
g238 | Oibita | Guatiguara_220 | b84 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 20 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | SANTANDER
g239 | San Bartolome | Guatiguara_220 | b84 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 20 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | SANTANDER
g240 | Sta Rosa | Paipa_220 | b75 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 20 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | BOYCASAN
g241 | Altamira | Paipa_220 | b75 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 20 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | BOYCASAN
g242 | Innercol I | San_Antonio_220 | b120 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 0 | 90 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | BOYCASAN
g243 | PCH La Libertad | Paipa_220 | b75 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 1.2 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | NORDESTE | BOYCASAN
g244 | Puente Guillermo | Paipa_220 | b75 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 1 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | NORDESTE | BOYCASAN
g245 | Menor Termobolivar | San_Antonio_220 | b120 | 0 | 0 | 0 | 0 | 0.48 | 0.8 | 3 | 9.7 | -4.35 | 2 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | BOYCASAN
g246 | Termomechero 4 U1 | San_Antonio_220 | b120 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 5.55 | 9.65 | -9.65 | 5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | BOYCASAN
g247 | Termomechero 5 U1 | San_Antonio_220 | b120 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 5.55 | 9.65 | -9.65 | 5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | BOYCASAN
g248 | Termomechero 6 U1 | San_Antonio_220 | b120 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 5.55 | 9.65 | -9.65 | 5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | BOYCASAN
g249 | Autog Argos Sogamoso | San_Antonio_220 | b120 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 5 | -11.25 | 11.25 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | BOYCASAN
g250 | Termomechero 4 U2 | San_Antonio_220 | b120 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 5.55 | 9.65 | -9.65 | 5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | BOYCASAN
g251 | Termomechero 5 U2 | San_Antonio_220 | b120 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 5.55 | 9.65 | -9.65 | 5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | BOYCASAN
g252 | Termomechero 6 U2 | San_Antonio_220 | b120 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 5.55 | 9.65 | -9.65 | 5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | BOYCASAN
g253 | Tasajero | Tasajero_220 | b80 | 0 | 0 | 0 | 0 | 20 | 0.85 | 68 | 163 | -57.4286 | 113.7551 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | NORDESTE | NSANTAND
g254 | Tasajero II | Tasajero_220 | b80 | 0 | 0 | 0 | 0 | 15.75 | 0.85 | 66 | 170 | -65 | 120 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | NSANTAND
g255 | Menor Palmas SGil | Palos_220 | b88 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 15 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | NORDESTE | SANTANDER
g256 | Sogamoso 3 | Sogamoso_220 | b87 | 0 | 0 | 0 | 0 | 16.5 | 0.9 | 116.6 | 273 | -142.9726 | 150.3151 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | NORDESTE | SANTANDER
g257 | Sogamoso 2 | Sogamoso_220 | b87 | 0 | 0 | 0 | 0 | 16.5 | 0.9 | 116.6 | 273 | -142.9726 | 150.3973 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | SANTANDER
g258 | Sogamoso 1 | Sogamoso_220 | b87 | 0 | 0 | 0 | 0 | 16.5 | 0.9 | 116.6 | 273 | -142.9726 | 150.1918 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | SANTANDER
g259 | Merilectrica | Comuneros_220 | b83 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 90 | 167 | -79 | 123 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | SANTANDER
g260 | Menor Cascada EPM | Guatiguara_220 | b84 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 3 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | SANTANDER
g261 | Autog Ecopetrol | Comuneros_220 | b83 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 15 | 0 | 10 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | SANTANDER
g262 | PCH Mulatos | Ancon_EPM_220 | b105 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 9.23 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g263 | Gen CAA | Ancon_EPM_220 | b105 | 0 | 0 | 0 | 0 | 13.8 | 0.91 | 0 | 80 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g264 | Gen CAB | Ancon_EPM_220 | b105 | 0 | 0 | 0 | 0 | 13.8 | 0.91 | 0 | 36 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g265 | Gen CARG | Ancon_EPM_220 | b105 | 0 | 0 | 0 | 0 | 13.8 | 0.91 | 0 | 55 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g266 | Escuela de Minas 1 | Oriente_220 | b104 | 0 | 0 | 0 | 0 | 13.8 | 0.957 | 0 | 19 | -3.06 | 5.09 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g267 | Escuela de Minas 2 | Oriente_220 | b104 | 0 | 0 | 0 | 0 | 13.8 | 0.957 | 0 | 18 | -3.06 | 5.09 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g268 | Escuela de Minas 3 | Oriente_220 | b104 | 0 | 0 | 0 | 0 | 13.8 | 0.957 | 0 | 18 | -3.06 | 5.09 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g269 | Menor La Paloma | Oriente_220 | b104 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 13.6 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g270 | PCH SAndres Cuerquia 19.9 1 | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 9.95 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g271 | PCH SAndres Cuerquia 19.9 2 | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 9.95 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g272 | PCH La Chorrera 15 MW | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 15 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g273 | Autog Nare-Argos 9MW | Playas_220 | b100 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 9 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g274 | PCH Las Violetas 0.945 MW | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.945 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g275 | Menor Hidronare | Playas_220 | b100 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 14 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g276 | PCH Conde | Ancon_EPM_220 | b105 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 3.52 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g277 | PCH Mulatos II | Ancon_EPM_220 | b105 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 7.34 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g278 | Aut Familia | Guayabal_220 | b113 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 1 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g279 | PCH Pocune | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.2 | 0.8 | 0 | 1 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g280 | Ayura | Ancon_EPM_220 | b105 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 18 | -0.1 | 7 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g281 | Menor Cementos Nare | Playas_220 | b100 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 4.5 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g282 | La Herradura 1 | Occidente_220 | b94 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 0 | 10 | -5 | 5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g283 | Menor La Vuelta | Occidente_220 | b94 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 0 | 11.6 | -5 | 5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g284 | Menor Niquia | Bello_220 | b107 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 19 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g285 | Menor P Blancas | Miraflores_220 | b109 | 0 | 0 | 0 | 0 | 13.2 | 0.8 | 0 | 5 | -0.1 | 3 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g286 | Menor Pajarito U1 | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 4.9 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g287 | Riogrande 1 | Bello_220 | b107 | 0 | 0 | 0 | 0 | 6.9 | 0.94 | 0 | 19 | -0.1 | 12 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g288 | Menor Riogrande | Bello_220 | b107 | 0 | 0 | 0 | 0 | 6.9 | 0.89 | 0 | 0.3 | 0 | 12 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g289 | Guadalupe III 1 | Guadalupe_220 | b102 | 0 | 0 | 0 | 0 | 13.8 | 0.957 | 0 | 45 | -18.281 | 19.4486 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g290 | Guadalupe IV 1 | Guadalupe_220 | b102 | 0 | 0 | 0 | 0 | 13.8 | 0.99 | 35 | 75 | -35.1738 | 38.0993 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g291 | Guadalupe IV 2 | Guadalupe_220 | b102 | 0 | 0 | 0 | 0 | 13.8 | 0.99 | 35 | 75 | -35.1738 | 38.0993 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g292 | Guadalupe IV 3 | Guadalupe_220 | b102 | 0 | 0 | 0 | 0 | 13.8 | 0.99 | 35 | 75 | -35.1738 | 38.0993 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g293 | Guatape 1 | Guatape_220 | b91 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 70 | -14 | 32 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g294 | Guatape 2 | Guatape_220 | b91 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 70 | -32 | 32 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g295 | Guatape 3 | Guatape_220 | b91 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 70 | -14 | 32 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g296 | Guatape 4 | Guatape_220 | b91 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 70 | -14 | 32 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g297 | Guatape 5 | Guatape_220 | b91 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 0 | 70 | -14 | 32 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g298 | Guatape 6 | Guatape_220 | b91 | 0 | 0 | 0 | 0 | 13.8 | 0.93 | 0 | 70 | -14 | 32 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g299 | Guatape 7 | Guatape_220 | b91 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 0 | 70 | -14 | 32 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g300 | Guatape 8 | Guatape_220 | b91 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 0 | 70 | -14 | 32 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g301 | La Tasajera 1 | La_Tasajera_220 | b93 | 0 | 0 | 0 | 0 | 13.8 | 0.95 | 0 | 102 | -30.098 | 34.7843 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g302 | San Carlos 1 | San_Carlos_500 | b98 | 0 | 0 | 0 | 0 | 16.5 | 0.95 | 22 | 155 | -55.9038 | 58.9808 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g303 | San Carlos 3 | San_Carlos_500 | b98 | 0 | 0 | 0 | 0 | 16.5 | 0.95 | 22 | 155 | -55.9038 | 59.0769 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g304 | San Carlos 5 | San_Carlos_220 | b97 | 0 | 0 | 0 | 0 | 16.5 | 0.95 | 22 | 155 | -55.9038 | 57.8846 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g305 | San Carlos 7 | San_Carlos_500 | b98 | 0 | 0 | 0 | 0 | 16.5 | 0.95 | 22 | 155 | -55.9038 | 57.8846 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g306 | Sierra Gas 1 | La_Sierra_220 | b92 | 0 | 0 | 0 | 0 | 18 | 0.85 | 89 | 145 | -71 | 114 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g307 | Calderas 1 | Guatape_220 | b91 | 0 | 0 | 0 | 0 | 13.2 | 0.95 | 0 | 9.95 | -5 | 5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g308 | Menor Cascada | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 2.3 | -0.012 | 0.6 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g309 | Menor R Piedras 1 | Ancon_EPM_220 | b105 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 10 | -2 | 2 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g310 | Troneras 1 | Guadalupe_220 | b102 | 0 | 0 | 0 | 0 | 6.6 | 0.85 | 1 | 21 | -11.7833 | 12.6167 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g311 | Jaguas 1 | Jaguas_220 | b99 | 0 | 0 | 0 | 0 | 13.8 | 0.95 | 15 | 85 | -33 | 28 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g312 | La Tasajera 2 | La_Tasajera_220 | b93 | 0 | 0 | 0 | 0 | 13.8 | 0.95 | 0 | 102 | -30.098 | 34.7843 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g313 | La Tasajera 3 | La_Tasajera_220 | b93 | 0 | 0 | 0 | 0 | 13.8 | 0.95 | 0 | 102 | -30.098 | 34.7843 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g314 | Playas 1 | Playas_220 | b100 | 0 | 0 | 0 | 0 | 13.8 | 0.96 | 55 | 69 | -29 | 27 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g315 | Porce 1 | Porce_220 | b103 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 75 | 135 | -66.6333 | 75.5667 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g316 | Menor Santiago 1 | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 1.4 | -0.012 | 0.6 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g317 | PCH Agua Fresca | Ancon_EPM_220 | b105 | 0 | 0 | 0 | 0 | 4.16 | 0.9 | 0.72 | 7.29 | 0 | 1.05 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g318 | PCH Caruquia | Bello_220 | b107 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 3.9 | 9.5 | -4.02 | 5.12 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g319 | PCH Guanaquitas | Bello_220 | b107 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 3.89 | 9.5 | -4.02 | 5.12 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g320 | PCH Santa Rita | Ancon_EPM_220 | b105 | 0 | 0 | 0 | 0 | 13.2 | 0.8 | 0 | 1.3 | -0.012 | 0.6 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g321 | PCH Hidromontañitas 1 | Bello_220 | b107 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 10 | -5 | 3 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g322 | Centro Gas 1 | Termo_Centro_220 | b106 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 30 | 97 | -57.3828 | 79.2594 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g323 | Centro Gas 2 | Termo_Centro_220 | b106 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 30 | 97 | -57.3828 | 79.2594 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g324 | Centro Vapor | Termo_Centro_220 | b106 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 30 | 85 | -56 | 96.8889 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g325 | Porce III 1 | Porce_III_500 | b111 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 125 | 180 | -106.7284 | 97.8519 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g326 | Porce III 2 | Porce_III_500 | b111 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 125 | 180 | -106.7284 | 97.8519 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g327 | Porce III 3 | Porce_III_500 | b111 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 125 | 180 | -106.7284 | 97.8519 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g328 | Porce III 4 | Porce_III_500 | b111 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 125 | 190 | -106.8333 | 98.1667 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g329 | San Carlos 2 | San_Carlos_220 | b97 | 0 | 0 | 0 | 0 | 16.5 | 0.95 | 22 | 155 | -55.9038 | 59.0769 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g330 | San Carlos 4 | San_Carlos_500 | b98 | 0 | 0 | 0 | 0 | 16.5 | 0.95 | 22 | 155 | -55.9038 | 58.0769 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g331 | San Carlos 6 | San_Carlos_500 | b98 | 0 | 0 | 0 | 0 | 16.5 | 0.95 | 22 | 155 | -55.9038 | 59.0769 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g332 | San Carlos 8 | San_Carlos_500 | b98 | 0 | 0 | 0 | 0 | 16.5 | 0.95 | 22 | 155 | -55.9038 | 59.0769 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g333 | Sierra Vapor | La_Sierra_220 | b92 | 0 | 0 | 0 | 0 | 18 | 0.85 | 61 | 158 | -231 | 231 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g334 | PCH Barroso 1 | Ancon_EPM_220 | b105 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 0.54 | 9.95 | -5.8 | 6.2 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g335 | Playas 2 | Playas_220 | b100 | 0 | 0 | 0 | 0 | 13.8 | 0.96 | 55 | 69 | -29 | 26 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g336 | Playas 3 | Playas_220 | b100 | 0 | 0 | 0 | 0 | 13.8 | 0.96 | 55 | 69 | -29 | 27 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g337 | Porce 2 | Porce_220 | b103 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 75 | 135 | -66.6333 | 75.5667 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g338 | Porce 3 | Porce_220 | b103 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 75 | 135 | -66.6333 | 75.5667 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g339 | Jaguas 2 | Jaguas_220 | b99 | 0 | 0 | 0 | 0 | 13.8 | 0.95 | 15 | 85 | -65 | 50 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g340 | Guadalupe III 2 | Guadalupe_220 | b102 | 0 | 0 | 0 | 0 | 13.8 | 0.957 | 0 | 45 | -18.281 | 19.4486 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g341 | Guadalupe III 3 | Guadalupe_220 | b102 | 0 | 0 | 0 | 0 | 13.8 | 0.957 | 0 | 45 | -18.281 | 19.4486 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g342 | Guadalupe III 4 | Guadalupe_220 | b102 | 0 | 0 | 0 | 0 | 13.8 | 0.957 | 0 | 45 | -18.281 | 19.4486 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g343 | Guadalupe III 5 | Guadalupe_220 | b102 | 0 | 0 | 0 | 0 | 13.8 | 0.957 | 0 | 45 | -18.281 | 19.4486 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g344 | Guadalupe III 6 | Guadalupe_220 | b102 | 0 | 0 | 0 | 0 | 13.8 | 0.957 | 0 | 45 | -18.281 | 19.4486 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g345 | Troneras 2 | Guadalupe_220 | b102 | 0 | 0 | 0 | 0 | 6.6 | 0.85 | 1 | 21 | -11.7833 | 12.6167 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g346 | Sierra Gas 2 | La_Sierra_220 | b92 | 0 | 0 | 0 | 0 | 18 | 0.85 | 89 | 142 | -71 | 114 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g347 | Calderas 2 | Guatape_220 | b91 | 0 | 0 | 0 | 0 | 13.2 | 0.95 | 0 | 9.95 | -5 | 5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g348 | PCH Hidromontañitas 2 | Bello_220 | b107 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 9.9 | -5 | 3 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g349 | La Herradura 2 | Occidente_220 | b94 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 0 | 10 | -5 | 5 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g350 | Menor Santiago 2 | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 1.4 | -0.012 | 0.6 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g351 | PCH Barroso 2 | Ancon_EPM_220 | b105 | 0 | 0 | 0 | 0 | 13.8 | 0.85 | 0.54 | 9.95 | -5.8 | 6.2 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g352 | Carlos Lleras G1 | Barbosa_220 | b101 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 15.6 | 39 | -42.5 | 28.2 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g353 | San Miguel U1 | Guatape_220 | b91 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 9.45 | 22 | -20.8062 | 18.7538 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g354 | PCH Abejorral | Oriente_220 | b104 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 3 | -2.64 | 2.31 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g355 | PCH El Popal G1 | Guatape_220 | b91 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 9.95 | -11.223 | 8.729 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g356 | PCH El Popal G2 | Guatape_220 | b91 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 9.95 | -11.223 | 8.729 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g357 | PCH San Matias G1 | Guatape_220 | b91 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 5.76 | 9.95 | -1 | 1 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g358 | PCH San Matias G2 | Guatape_220 | b91 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 5.76 | 9.95 | -1 | 1 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g359 | PCH El Molino G1 | Guatape_220 | b91 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 5.76 | 9.95 | -2 | 2 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g360 | PCH El Molino G2 | Guatape_220 | b91 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 5.76 | 9.95 | -2 | 2 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g361 | San Miguel U2 | Guatape_220 | b91 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 9.45 | 22 | -20.8062 | 18.7538 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g362 | Cog Coltejer | Envigado_220 | b108 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 9.4 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g363 | PCH Cantayus U1 | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 4.16 | 0.9 | 0.9 | 2.16 | 0 | 1 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g364 | Carlos Lleras G2 | Barbosa_220 | b101 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 15.6 | 39 | -42.5 | 28.2 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g365 | PCH Barrancas | Occidente_220 | b94 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 4.7 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g366 | PCH Luzma I U2 | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 10 | -5.384 | 5.384 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g367 | PCH Luzma II U2 | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 10 | -5.384 | 5.384 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g368 | PCH Doña Teresa | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 1.765 | 8.5 | -5.565 | 7.98 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g369 | Menor R Piedras 2 | Ancon_EPM_220 | b105 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 9.9 | -2 | 2 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g370 | PCH Magallo | Ancon_EPM_220 | b105 | 0 | 0 | 0 | 0 | 6.9 | 0.9 | 0.5 | 5.7 | -2.871 | 2.97 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g371 | Menor America | Occidente_220 | b94 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.41 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g372 | Menor Campestre EPM | Guayabal_220 | b113 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.87 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g373 | Menor Nutibara | Occidente_220 | b94 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.75 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g374 | Menor Amalfi | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.81 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g375 | Menor Bello | Bello_220 | b107 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.35 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g376 | Menor Manantiales | Occidente_220 | b94 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 3.15 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g377 | Menor Caracoli | Malena_220 | b112 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 2.6 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g378 | Menor SJose Montaña | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.4 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g379 | Menor Sonson | Oriente_220 | b104 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 18.5 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g380 | Menor Rio Frio Tamesis | Ancon_EPM_220 | b105 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 1 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g381 | PCH Las Palmas U1 | Bello_220 | b107 | 0 | 0 | 0 | 0 | 4.16 | 0.9 | 0 | 1.4 | -1.08 | 1.2 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g382 | Autog El Cairo | Ancon_EPM_220 | b105 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 3.5 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g383 | Menor La Rebusca | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.7 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g384 | PCH Juan Garcia U1 | Occidente_220 | b94 | 0 | 0 | 0 | 0 | 4.16 | 0.9 | 0 | 2.26 | -1.6 | 1.89 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g385 | PCH Porce III | Guadalupe_220 | b102 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 1.031 | 1.8 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g386 | Menor Remedios | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 0.75 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g387 | Menor Urrao | Ancon_EPM_220 | b105 | 0 | 0 | 0 | 0 | 13.8 | 0.8 | 0 | 1.03 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g388 | PCH Alejandria | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 15 | -7.31 | 10.2 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g389 | PCH Cantayus U2 | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 4.16 | 0.9 | 0.9 | 2.16 | 0 | 1 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g390 | PCH Las Palmas U2 | Bello_220 | b107 | 0 | 0 | 0 | 0 | 4.16 | 0.9 | 0 | 1.4 | -1.08 | 1.2 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g391 | PCH Luzma I U1 | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 9.6 | -5.384 | 5.384 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g392 | PCH Luzma II U1 | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 9.6 | -5.384 | 5.384 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g393 | Menor SJose Montaña II | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 0.48 | 1 | 0.5 | 1.1 | -0.52 | 0.52 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g394 | PCH Aures Bajo U1 | Oriente_220 | b104 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 9.7 | -4.473 | 4.87 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g395 | PCH Aures Bajo U2 | Oriente_220 | b104 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 9.7 | -4.473 | 4.87 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 1 | ANTIOQUIA | ANTIOQUI
g396 | PCH Juan Garcia U2 | Occidente_220 | b94 | 0 | 0 | 0 | 0 | 4.16 | 0.9 | 0 | 2.26 | -1.6 | 1.89 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
g397 | Menor Pajarito U2 | El_Salto_220 | b110 | 0 | 0 | 0 | 0 | 13.8 | 0.9 | 0 | 8.3 | 0 | 3.48 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
gs1 | Gen Solar II PNuevo 9.9 MW | Sabanalarga_500 | b4 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 10 | -3.333 | 3.333 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | ATLANTIC
gs2 | Gen Solar Ponedera 9.9MW | Sabanalarga_220 | b3 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 10 | -3.333 | 3.333 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | ATLANTIC
gs3 | Gen Solar I PNuevo 19.3 MW | Sabanalarga_500 | b4 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | ATLANTIC
gs4 | Gen Solar Prosperidad 19.5MW | Sabanalarga_500 | b4 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | ATLANTIC
gs5 | Gen Solar Bosques 1 19.9MW | Sabanalarga_220 | b3 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | ATLANTIC
gs6 | Gen Solar Bosques 2 19.9MW | Sabanalarga_220 | b3 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | ATLANTIC
gs7 | Gen Solar Bosques 3 19.9MW | Sabanalarga_220 | b3 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | ATLANTIC
gs8 | Gen Solar Baranoa 19.9 MW | Sabanalarga_500 | b4 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | ATLANTIC
gs9 | Gen Solar El Colibri 19.9 MW | Nva_Barranquilla_220 | b2 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | ATLANTIC
gs10 | Gen Solar Atlantico I 30 MW | Nva_Barranquilla_220 | b2 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 34 | -11.3322 | 11.3322 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | ATLANTIC
gs11 | Gen Solar Guayepo 1 200 MW | Sabanalarga_500 | b4 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 224 | -74.6592 | 74.6592 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | ATLANTIC
gs12 | Gen Solar Sabana 200 MW | Sabanalarga_220 | b3 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 224 | -74.6592 | 74.6592 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | ATLANTIC
gs13 | Gen Solar Bosq de Bolivar 503 19.9MW | Sabanalarga_500 | b4 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | ATLANTIC
gs14 | Gen Solar Bosq de Bolivar 504 19.9MW | Sabanalarga_500 | b4 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | ATLANTIC
gs15 | Gen Solar La Iguana 19.5MW | Ternera_220 | b12 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | BOLIVAR
gs16 | Gen Solar Bayunca 3 MW | Bolivar_220 | b10 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 3 | -0.9999 | 0.9999 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | BOLIVAR
gs17 | Gen Solar Bayunca 9.9 MW | Bolivar_500 | b9 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 15 | -4.9995 | 4.9995 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | BOLIVAR
gs18 | Gen Solar Zambrano II 15.5 MW | Bolivar_220 | b10 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 24 | -7.9992 | 7.9992 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | BOLIVAR
gs19 | Gen Solar Bolivar 8.185 MW | Bolivar_500 | b9 | 0 | 0 | 0 | 0 | 0.63 | 1 | 0.08185 | 8.06 | -2.6864 | 2.6864 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | BOLIVAR
gs20 | Solar CSF 90MW | San_Felipe_220 | b33 | 0 | 0 | 0 | 0 | 0.4 | 1 | 0.9 | 90 | -29.997 | 29.997 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | CQR
gs21 | Gen Solar Continua Cartago 99MW | Cartago_220 | b55 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 100 | -33.33 | 33.33 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
gs22 | Solar Yumbo 9.8MW | Yumbo_220 | b48 | 0 | 0 | 0 | 0 | 0.4 | 1 | 0.09 | 9.8 | -3.2663 | 3.2663 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | SUROCCIDENTAL | VALLE
gs23 | Windpeshi 200MW | Cuestecita_220 | b60 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 200 | -66.66 | 66.66 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
gs24 | Guajira I 20MW | Cuestecita_220 | b60 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
gs25 | Wayuu 12MW | Cuestecita_220 | b60 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 12 | -3.9996 | 3.9996 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
gs26 | Gen Solar LATAMS1 19.9MVA | Valledupar_220 | b63 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
gs27 | Gen Solar LATAMS2 9.9MVA | Valledupar_220 | b63 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 10 | -3.333 | 3.333 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
gs28 | Gen Solar El Paso 70MW | La_Loma_500 | b117 | 0 | 0 | 0 | 0 | 33 | 1 | 0 | 70 | -23.331 | 23.331 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
gs29 | Gen LATAMSOLAR 150MW | La_Loma_500 | b117 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 150 | -49.995 | 49.995 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
gs30 | Solar Petalo 9.9MW | La_Loma_500 | b117 | 0 | 0 | 0 | 0 | 0.4 | 1 | 0.09 | 9.8 | -3.2663 | 3.2663 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
gs31 | Gen Solar Fundacion 100MW | Fundacion_220 | b58 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 100 | -33.33 | 33.33 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
gs32 | Gen Solar Codazzi 2 19.9MW | Valledupar_220 | b63 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
gs33 | Gen Solar Codazzi 1 19.9MW | Valledupar_220 | b63 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | GCM
gs34 | Gen Solar Since 19.99 MW | Chinu_220 | b118 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | CORDOSUC
gs35 | Gen Solar Sierpe 19.99 MW | Chinu_500 | b66 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | CORDOSUC
gs36 | Gen Solar Guayacan 8 MW | Chinu_220 | b118 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 8 | -2.6664 | 2.6664 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | CORDOSUC
gs37 | Gen Solar La Ceiba 8 MW | Bolivar_220 | b10 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 8 | -2.6664 | 2.6664 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | BOLIVAR
gs38 | Morrosquillos I 19.99 MW | Bolivar_220 | b10 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | BOLIVAR
gs39 | Morrosquillos II 19.99 MW | Bolivar_220 | b10 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | BOLIVAR
gs40 | Gen Solar La Cayena 19.9 MW | Chinu_220 | b118 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | CORDOSUC
gs41 | Gen Solar La Union 100 MW | Monteria_220 | b119 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 112 | -37.3296 | 37.3296 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | CORDOSUC
gs42 | Gen Solar Filigrana 9.9 MW | Chinu_220 | b118 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 10 | -3.333 | 3.333 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | CARIBE | CORDOSUC
gs43 | Solar Bosques 1 19.9MW | Reforma_220 | b70 | 0 | 0 | 0 | 0 | 0.4 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | META
gs44 | Solar Bosques 2 19.9MW | Reforma_220 | b70 | 0 | 0 | 0 | 0 | 0.4 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | META
gs45 | Solar Bosques 3 19.9MW | Reforma_220 | b70 | 0 | 0 | 0 | 0 | 0.4 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | META
gs46 | Solar Bosques 4 19.9MW | Reforma_220 | b70 | 0 | 0 | 0 | 0 | 0.4 | 1 | 0 | 20 | -6.666 | 6.666 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | META
gs47 | Solar Bosques 5 17.9MW | Reforma_220 | b70 | 0 | 0 | 0 | 0 | 0.4 | 1 | 0 | 18 | -5.9994 | 5.9994 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ORIENTAL | META
gs48 | Solar Paipa I 88MW | Paipa_220 | b75 | 0 | 0 | 0 | 0 | 0.4 | 1 | 0.44 | 88 | -29.3304 | 29.3304 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | BOYCASAN
gs49 | Solar Paipa II 72MW | Paipa_220 | b75 | 0 | 0 | 0 | 0 | 0.4 | 1 | 0.36 | 72 | -23.9976 | 23.9976 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | NORDESTE | BOYCASAN
gs50 | Gen Solar Porton del Sol 102MW | Purnio_220 | b96 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 102 | -33.9966 | 33.9966 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI
gs51 | Gen Solar La Sierra 200MW | La_Sierra_220 | b92 | 0 | 0 | 0 | 0 | 0.69 | 1 | 0 | 200 | -66.66 | 66.66 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | ANTIOQUIA | ANTIOQUI

## load_factor
| max_factor | Qd_factor
b4 | 0.0020608 | 0.3614
b7 | 0 | 0
b9 | 0.0018766 | 0.37622
b15 | 0 | 0
b29 | 0.0075322 | 0.40404
b56 | 2.6032e-05 | 0.44295
b58 | 0.0034337 | 0.50977
b61 | 0.00052857 | 0.33601
b115 | 0.00092567 | 0.48432
b67 | 0.0012923 | 0.37066
b73 | 6.7138e-05 | 0.29167
b74 | 0.0012091 | 0.38502
b76 | 0.0018304 | 0.82535
b80 | 0 | 0
b14 | 0.0067692 | 0.38091
b83 | 0 | 0
b85 | 0.0056654 | 0.61646
b112 | 0.001342 | 0.41001
b91 | 0.00022327 | 0.33179
b102 | 0.00032124 | 0.27817
b99 | 0 | 0
b116 | 0.0069863 | 0.42185
b8 | 0.016329 | 0.32665
b82 | 0.0074261 | 0.37301
b84 | 0.0048239 | 0.41957
b88 | 0.0035909 | 0.53159
b36 | 0.0037621 | 0.20574
b97 | 0.00046273 | 0.40917
b92 | 0.0040982 | 0.36737
b10 | 0.004971 | 0.38392
b94 | 0.023135 | 0.40625
b96 | 0.0025943 | 0.39147
b100 | 0.0015431 | 0.29644
b101 | 0.0048394 | 0.34152
b104 | 0.015362 | 0.33083
b105 | 0.012627 | 0.3578
b107 | 0.012192 | 0.38938
b108 | 0.014132 | 0.44013
b109 | 0.013787 | 0.37156
b110 | 0.0069126 | 0.3048
b113 | 0.018773 | 0.36125
b13 | 0.0049711 | 0.55852
b16 | 0.0074495 | 0.38224
b19 | 0.027643 | 0.29512
b20 | 0.0022003 | 0.38906
b21 | 0.0011686 | 0.34108
b23 | 0.022175 | 0.29912
b1 | 0.027881 | 0.37904
b25 | 0.03559 | 0.31558
b26 | 0.054981 | 0.29921
b28 | 0.026745 | 0.34526
b30 | 0.011059 | 0.2979
b31 | 0.0036587 | 0.48792
b32 | 0.0098897 | 0.36075
b2 | 0.002976 | 0.26835
b33 | 0.0041213 | 0.2277
b34 | 0.0067346 | 0.29843
b39 | 0.0092327 | 0.47674
b40 | 0.0145 | 0.27521
b41 | 0.0084895 | 0.31587
b3 | 0.0065328 | 0.42604
b43 | 0.0084282 | 0.3422
b44 | 0.013648 | 0.48551
b45 | 0.021686 | 0.43564
b46 | 0.0030588 | 0.26578
b47 | 0.0026761 | 0.37745
b48 | 0.038113 | 0.27317
b49 | 0.005051 | 0.33207
b52 | 0.012934 | 0.33487
b53 | 0.0048738 | 0.27398
b55 | 0.01047 | 0.21053
b57 | 0.002799 | 0.46319
b5 | 0.024062 | 0.41029
b60 | 0.013782 | 0.31251
b62 | 0.018771 | 0.4225
b65 | 0.0047348 | 0.46337
b6 | 0.0065396 | 0.5328
b66 | 0.0060324 | 0.37301
b68 | 0.014755 | 0.21599
b69 | 0.0069351 | 0.42468
b118 | 0.011659 | 0.42405
b119 | 0.011497 | 0.38664
b71 | 0.0013325 | 0.4904
b72 | 0.0067356 | 0.41044
b75 | 0.012471 | 0.47319
b120 | 0.014926 | 0.41138
b77 | 0.0012269 | 0.35873
b78 | 0.010449 | 0.43758
b79 | 0.0052903 | 0.41447
b12 | 0.031355 | 0.39681
b17 | 0.024888 | 0.3647
b27 | 0.015468 | 0.27153
b38 | 0.0196 | 0.33629
b50 | 0.036226 | 0.26568
b63 | 0.02724 | 0.41036
b70 | 0.027162 | 0.38281
b81 | 0.021675 | 0.3574